{"text_format":"1","workbook":"xlsx","n_sheets":45,"sheets":["Общая","РТМ","Подробная","КПСР 100,110","КПСР 200","КПСР 210","КССР","РА 100,200","Серия 110-VB2","Серия VFM2","Серия VL2","Серия VFS2","Серия VFG2_25","Серия VFG2_40","Серия VFGS2_16","Серия VFGS2_25","Серия VFGS2_40","Серия VM2","Серия VRB2","Серия VRG2","Серия VL3","Серия VF3","Серия VRB3","Серия VRG3","Серия AVP","Серия DPR","Серия AVA","Серия AVD","Серия AVDS","Серия AFP-VFG2_16","Серия AFP-VFG2_25","Серия AFA-VFG2_16","Серия AFA-VFG2_25","Серия AFD-VFG2_16","Серия AFD-VFG2_25","Привода","KVs","Перепад","Диапазоны","КПСР серия 100","КПСР серия 110","КПСР серия 200","КПСР серия 210","КССР серия 100","РА серия 100,200"],"not_rendered":{"charts":0,"images":96,"macros":1,"external_links":0,"defined_names":70,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Общая","index":0,"n_rows":30,"n_cols":13,"rows_kept":30,"cut":false,"hidden":false,"merged":[[0,12,1,12],[0,10,1,11],[4,0,7,0],[8,1,10,1],[20,5,23,5],[8,0,10,0],[11,0,13,0],[0,1,1,1],[0,2,1,2],[16,0,16,13],[17,0,17,13],[18,0,18,13]]}
[null,"Серия 100","Серия 110",null,null,null,null,null,null,null,"Серия 200",null,"Серия 210"]
[]
[]
[]
["Клапаны проходные седельные регулирующие по типу КПСР"]
[]
[]
[]
["Регуляторы давления прямого действия по типу РА",null,null,null,null,null,null,null,null,null,null,null,"Регуляторы РА-Р"]
[]
[]
["Клапаны смесительные/ разделительные регулирующие по типу КССР"]
[]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]
[]
[]
[null,null,null,"до DN 100"]
[]
[]
[]
[null,null,null,"до DN 100"]
[]
[]
[]
[null,null,null,"до DN 100"]

{"sheet":"РТМ","index":1,"n_rows":26,"n_cols":5,"rows_kept":26,"cut":false,"hidden":false,"merged":[[23,1,23,4],[24,1,24,4],[25,1,25,4],[1,3,2,3],[1,4,2,4],[11,1,14,1],[18,1,19,1],[18,2,19,2],[1,1,2,1],[1,2,2,2]]}
[]
[null,"Параметр","РТМ-03А","ECL210","ECL310"]
[]
[null,"Число контуров регулирования","3+ контур подпитки",3,3]
[null,"Параметры выходов","Релейный, 220 В, 50 Гц, 2 А","Релейный, 220 В, 50 Гц, 2 А","Релейный, 220 В, 50 Гц, 2 А"]
[null,"Количество дискретных выходов",4,4,4]
[null,"Количество аналоговых выходов","4, 0-10 В","3, 0-10 В","3, 0-10 В"]
[null,"Количество дискретных входов",8,6,6]
[null,"Количество аналоговых входов","4, 0-10 В или 4-20 мА","2, 0-10 В или 4-20 мА","4, 0-10 В или 4-20 мА"]
[null,"Максимальное количество подключаемых датчиков температуры",8,6,6]
[null,"Диапазон измеряемых датчиком температур","от минус 50 до плюс 150 ºС","от минус 60 до плюс 150 ºС","от минус 60 до плюс 150 ºС"]
[null,"Типы регулирования","· горячей воды (постоянная температура)","· горячей воды (постоянная температура)","· горячей воды (постоянная температура)"]
[null,null," · по температурному графику","· по температурному графику","· по температурному графику"]
[null,null," · по температуре в помещении"]
[null,null," · по температурному графику с коррекцией по температуре в помещении"]
[null,"Режимы работы","· ручной · автоматический","· ручной · автоматический","· ручной · автоматический"]
[null,"Наличие архивов","Есть","Есть","Есть"]
[null,"Каналы последовательного интерфейса","RS-232, RS-485, Ethernet, оптический порт","RS-485","RS-485, Ethernet"]
[null,"Электропитание","(24 ± 5) В, 50 Гц","(24 ± 5) В, 50 Гц ","(24 ± 5) В, 50 Гц "]
[null,null,null,"~230 В; 50/60 Гц","~230 В; 50/60 Гц"]
[null,"Мощность, потребляемая электронным блоком, не более","5 Вт","5 Вт","5 Вт"]
[]
[]
[null,"По вопросам продаж и поддержки обращайтесь:"]
[]
[null,"Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Подробная","index":2,"n_rows":129,"n_cols":19,"rows_kept":129,"cut":false,"hidden":true,"merged":[[91,15,96,16],[96,13,96,14],[93,17,96,18],[54,9,54,10],[55,9,55,10],[56,9,56,10],[73,9,73,10],[71,3,72,4],[71,5,72,6],[71,7,72,8],[67,11,72,12],[72,13,72,14],[69,15,72,16],[69,17,72,18],[73,15,73,16],[82,3,87,3],[89,3,90,3],[91,3,92,3],[90,17,92,17],[88,15,89,15],[91,5,92,5],[80,9,80,10],[82,9,89,9],[82,13,86,13],[125,9,125,10],[122,9,122,10],[123,9,123,10],[124,9,124,10],[90,9,92,9],[97,9,100,10],[102,9,102,10],[103,9,103,10],[104,9,104,10],[105,9,105,10],[106,9,106,10],[112,9,120,10],[126,9,126,10],[127,9,127,10],[128,9,128,10],[0,5,0,6],[1,5,1,6],[2,5,2,6],[6,5,6,6],[7,5,7,6],[8,5,8,6],[19,5,20,5],[10,5,13,5],[21,5,22,5],[14,5,18,5],[30,5,30,6],[31,5,31,6],[32,5,32,6],[34,5,37,5],[38,5,42,5],[43,5,44,5],[107,9,107,10],[108,9,108,10],[109,9,109,10],[123,5,123,6],[121,9,121,10],[6,17,6,18],[7,17,7,18],[8,17,8,18],[10,15,15,15],[17,15,18,15],[19,15,20,15],[10,13,15,13],[17,13,20,13],[6,13,6,14],[10,17,17,17],[18,17,20,17],[67,15,68,15],[67,13,69,13],[8,9,8,10],[10,9,17,9],[18,9,20,9],[26,9,26,10],[27,9,27,10],[28,9,28,10],[82,17,89,17],[25,15,25,16],[32,17,32,18],[27,13,27,14],[58,13,62,13],[63,13,64,13],[65,13,66,13],[21,15,24,16],[56,17,56,18],[46,11,48,12],[48,13,48,14],[25,9,25,10],[21,9,24,10],[22,11,24,12],[21,13,24,14],[30,11,30,12],[25,17,25,18],[39,11,39,12],[40,11,40,12],[41,11,41,12],[42,11,42,12],[43,11,43,12],[44,11,44,12],[45,11,45,12],[55,13,55,14],[55,15,55,16],[55,17,55,18],[29,15,29,16],[29,17,29,18],[30,15,30,16],[30,17,30,18],[34,11,34,12],[35,11,35,12],[36,11,36,12],[37,11,37,12],[30,13,30,14],[38,11,38,12],[41,13,42,13],[43,13,45,13],[46,13,47,13],[25,13,25,14],[64,7,67,7],[21,17,24,18],[3,3,3,4],[4,3,4,4],[6,3,6,4],[0,1,0,2],[1,1,1,2],[2,1,2,2],[6,1,6,2],[49,17,49,18],[34,7,39,7],[34,15,39,15],[40,7,41,7],[41,15,42,15],[43,15,44,15],[31,17,31,18],[32,7,32,8],[32,11,32,12],[32,13,32,14],[32,15,32,16],[31,15,31,16],[9,11,9,12],[30,9,30,10],[10,7,15,7],[16,7,17,7],[25,7,25,8],[25,5,25,6],[7,1,7,2],[8,1,8,2],[28,1,28,2],[26,1,26,2],[26,3,26,4],[27,3,27,4],[27,1,27,2],[26,5,26,6],[27,5,28,6],[23,3,24,4],[23,5,24,6],[49,5,49,6],[28,7,28,8],[28,11,28,12],[49,11,49,12],[34,3,39,3],[19,7,24,8],[25,1,25,2],[30,1,30,2],[30,3,30,4],[30,7,30,8],[25,3,25,4],[6,7,6,8],[7,7,7,8],[7,9,7,10],[8,7,8,8],[7,3,7,4],[8,3,8,4],[49,13,49,14],[34,13,38,13],[40,3,42,3],[31,7,31,8],[31,11,31,12],[31,13,31,14],[29,0,29,14],[39,13,40,13],[18,11,18,12],[19,11,19,12],[20,11,20,12],[21,11,21,12],[25,11,25,12],[33,11,33,12],[46,1,48,2],[47,3,48,4],[47,5,48,6],[43,7,48,8],[6,9,6,10],[0,0,4,0],[3,1,3,2],[4,1,4,2],[0,11,0,12],[1,11,1,12],[2,11,2,12],[3,11,3,12],[4,11,4,12],[0,7,0,8],[1,7,1,8],[2,7,2,8],[3,7,3,8],[4,7,4,8],[0,9,0,10],[1,9,1,10],[2,9,2,10],[3,9,3,10],[4,9,4,10],[3,5,3,6],[4,5,4,6],[0,3,0,4],[1,3,1,4],[2,3,2,4],[0,17,0,18],[1,17,1,18],[2,17,2,18],[3,17,3,18],[4,17,4,18],[5,0,5,18],[6,15,6,16],[7,15,7,16],[8,15,8,16],[7,13,7,14],[8,13,8,14],[0,15,0,16],[1,15,1,16],[2,15,2,16],[3,15,3,16],[4,15,4,16],[6,11,6,12],[7,11,7,12],[8,11,8,12],[0,13,0,14],[1,13,1,14],[2,13,2,14],[3,13,3,14],[4,13,4,14],[52,9,52,10],[50,5,50,6],[51,5,52,6],[54,5,54,6],[52,13,52,14],[26,0,28,0],[26,7,26,8],[27,7,27,8],[26,11,26,12],[27,11,27,12],[26,13,26,14],[49,1,49,2],[49,3,49,4],[49,7,49,8],[32,1,32,2],[32,3,32,4],[31,1,31,2],[31,3,31,4],[28,3,28,4],[28,13,28,14],[31,9,31,10],[32,9,32,10],[49,9,49,10],[45,5,46,5],[73,13,73,14],[62,5,66,5],[58,7,63,7],[58,15,63,15],[65,15,66,15],[51,3,51,4],[51,7,51,8],[53,0,53,18],[54,1,54,2],[54,3,54,4],[54,7,54,8],[54,11,54,12],[54,13,54,14],[54,15,54,16],[54,17,54,18],[50,0,52,0],[50,1,50,2],[50,3,50,4],[50,7,50,8],[50,11,50,12],[50,13,50,14],[51,13,51,14],[50,9,50,10],[51,9,51,10],[55,1,55,2],[55,3,55,4],[55,7,55,8],[55,11,55,12],[78,13,78,14],[78,15,78,16],[78,17,78,18],[78,9,78,10],[73,17,73,18],[62,11,62,12],[55,5,55,6],[56,5,56,6],[56,1,56,2],[56,3,56,4],[56,7,56,8],[56,11,56,12],[56,13,56,14],[56,15,56,16],[58,5,61,5],[58,3,63,3],[64,3,66,3],[63,11,63,12],[69,7,70,7],[70,13,71,13],[74,0,76,0],[75,11,75,12],[74,13,74,14],[75,13,75,14],[74,15,74,16],[74,17,74,18],[75,17,75,18],[75,9,75,10],[76,9,76,10],[74,3,74,4],[74,7,74,8],[74,11,74,12],[74,1,74,2],[75,5,75,6],[76,5,76,6],[76,17,76,18],[88,1,89,1],[85,1,86,1],[74,9,74,10],[67,5,68,5],[69,5,70,5],[73,5,73,6],[74,5,74,6],[73,1,73,2],[73,3,73,4],[73,7,73,8],[79,5,79,6],[80,5,80,6],[82,5,87,5],[88,5,90,5],[77,0,77,18],[78,1,78,2],[78,3,78,4],[78,7,78,8],[78,11,78,12],[79,13,79,14],[78,5,78,6],[82,7,87,7],[88,7,89,7],[79,17,79,18],[127,5,127,6],[128,5,128,6],[115,7,116,8],[126,1,126,2],[121,3,121,4],[122,3,122,4],[123,3,123,4],[117,5,120,6],[128,1,128,2],[126,7,126,8],[127,7,127,8],[128,7,128,8],[126,3,126,4],[127,3,127,4],[124,5,124,6],[125,5,125,6],[126,5,126,6],[128,3,128,4],[118,3,118,4],[127,1,127,2],[80,1,80,2],[80,3,80,4],[80,7,80,8],[80,11,80,12],[80,13,80,14],[80,15,80,16],[80,17,80,18],[79,1,79,2],[79,3,79,4],[79,7,79,8],[79,15,79,16],[86,11,86,12],[87,11,87,12],[88,11,88,12],[89,11,89,12],[79,9,79,10],[94,13,95,13],[91,13,93,13],[110,9,110,10],[111,9,111,10],[93,11,93,12],[94,11,94,12],[91,11,91,12],[92,11,92,12],[81,11,81,12],[82,11,82,12],[83,11,83,12],[84,11,84,12],[85,11,85,12],[79,11,79,12],[90,11,90,12],[93,9,96,10],[95,11,95,12],[96,11,96,12],[89,13,90,13],[112,1,112,2],[113,1,113,2],[112,7,113,7],[121,1,121,2],[122,1,122,2],[123,1,123,2],[124,1,124,2],[102,5,102,6],[103,5,103,6],[104,5,104,6],[121,5,121,6],[122,5,122,6],[119,3,120,4],[105,3,105,4],[106,3,106,4],[107,3,107,4],[110,3,110,4],[111,3,111,4],[112,3,112,4],[113,3,113,4],[109,7,111,7],[106,7,108,7],[108,3,108,4],[91,1,92,1],[121,0,125,0],[125,1,125,2],[121,7,121,8],[122,7,122,8],[123,7,123,8],[124,7,124,8],[125,7,125,8],[114,1,114,2],[115,1,115,2],[116,1,116,2],[117,1,117,2],[124,3,124,4],[125,3,125,4],[118,1,120,2],[117,7,120,8],[116,3,116,4],[117,3,117,4],[114,3,114,4],[115,3,115,4],[92,7,96,8],[98,3,98,4],[99,3,99,4],[109,3,109,4],[10,11,10,12],[11,11,11,12],[12,11,12,12],[13,11,13,12],[14,11,14,12],[15,11,15,12],[16,11,16,12],[17,11,17,12],[73,11,73,12],[57,11,57,12],[58,11,58,12],[59,11,59,12],[60,11,60,12],[61,11,61,12],[64,11,64,12],[65,11,65,12],[66,11,66,12],[97,5,97,6],[98,5,98,6],[99,5,99,6],[100,5,100,6],[93,3,96,4],[93,5,96,6],[98,7,98,8],[99,7,99,8],[100,7,100,8],[93,1,96,2],[106,1,106,2],[107,1,107,2],[108,1,108,2],[109,1,109,2],[110,1,110,2],[111,1,111,2],[101,0,101,10],[102,1,102,2],[102,7,102,8],[103,1,103,2],[103,3,103,4],[103,7,103,8],[104,1,104,2],[104,3,104,4],[104,7,104,8],[102,3,102,4],[97,0,100,0],[97,1,97,2],[97,3,97,4],[98,1,98,2],[105,1,105,2],[100,3,100,4],[97,7,97,8]]}
["КПСР ","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM",null,"ADL",null,"TA",null,"Belimo",null,"Siemens"]
[null,"Серия 100 ",null,"VB 2",null,"STEVI 440",null,"Тип ZH",null,"RV 122",null,"Гранрег КМ125Ф",null,"CV206/216 GG",null,"H6xxN",null,"VVF42xx"]
[null,"Серия 110",null,"VFM 2",null,"STEVI 470/422",null,null,null,"RV 113 R",null,null,null,"CV216",null,"H6xxS",null,"VVF43xx"]
[null,null,null,"VF 2",null,null,null,null,null,"RV 2xx",null,null,null,null,null,"H6xxSP",null,"VVF53xx"]
[null,null,null,"VFG 2 /VFG 21"]
["Тех.характеристики"]
["ДУ max",400,null,250,null,250,null,100,null,150,null,200,null,150,null,150,null,150]
["Давление, бар","16 - 25",null,40,null,"16-40",null,"16-40",null,"6; 16; 25",null,16,null,"6; 16",null,"16; 25",null,16]
["t, °C, max",150,null,200,null,450,null,260,null,150,null,200,null,150,null,150,null,"150; 220"]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv 0,16..40","kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",5,"0,25; 0,4; 0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4",20,"1,6; 2,5; 4",4,null,14,"0,63; 1,25; 1,6; 2,5; 4",15,"0,4; 0,63; 1; 1,6; 2,5;4",20,"0,16 - 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",5,6.3,null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,6.3,5,null,null,"5; 6,3",null,"4; 6,3",null,6.3]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",7,10,null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,10,9,null,null,"8; 10",null,"6,3; 10",null,"5,0 - 10"]
[32,"10; 22","6,3; 10; 16",10,16,null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,16,15,null,null,"12,5; 16",null,"10; 16",null,16]
[40,"10; 25","10; 16; 25",10,25,30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,25,22,null,null,"20; 25",null,"16; 25",null,"12,5 - 25"]
[50,"10; 32","10; 16; 25; 32; 40",10,40,null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,40,40,null,null,"31,5; 40",null,"25; 40",null,"31,5; 40"]
[65,32,"25; 32; 40; 63",20,63,null,"40; 63","20; 38","16; 25; 40; 63",null,63,63,null,"20; 30","50; 63","18; 30","58; 63",null,"50; 63"]
[80,40,"40; 63; 80; 100",30,100,null,"63; 100",null,"25; 40; 63; 94",null,100,90,null,50,"80; 100",30,"90; 100",null,"80; 100"]
[100,50,"63; 80; 100; 125;160",30,160,null,"100; 160",38,"94; 125; 160",40,160,136,null,null,"125;160",null,"125; 145",40,"125; 160"]
[125,80,"100; 125; 160; 250",40,250,50,"160; 250",null,null,null,250,230,null,null,250,40,200,null,"200; 250"]
[150,80,"160; 250; 360",40,400,null,"250; 400",null,null,null,360,316,null,null,315,null,320,null,"315; 360; 400"]
[200,80,"250; 360; 450; 630",24,630,65,630,null,null,null,null,555]
[250,80,"400; 630; 800; 1000",24,900,null,1000]
[300,100,"1000; 1250; 1600"]
[400,100,"1250; 1600; 2000; 2500"]
["Разгрузка","Все диаметры",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 25-100",null,"Все диаметры",null,null,null,"Все диаметры",null,"частично разгружены ду 65-100",null,"С компенсацией давления с ду 50"]
["КПСР ","Серия 200",null,"VFS 2",null,"STEVI 440",null,"Тип ZH",null,"RV 21x",null,"Гранрег КМ125Ф",null,"CV225"]
[null,null,null,"VEFS 2",null,"STEVI 470/422"]
[null,null,null,"VFGS 2"]
["Тех.характеристики"]
["ДУ max",200,null,250,null,250,null,100,null,400,null,200,null,300]
["Давление, бар",25,null,25,null,"16-40",null,"16-40",null,"16; 40",null,16,null,"16-40"]
["t, °C, max",220,null,250,null,450,null,260,null,"300…500",null,200,null,200]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","kv",null,"ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",15,"0,4;0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4",null,null,4,null,20,"0,16; 0,25; 0,4 ;0,63; 1; 1,25; 1,6; 2,5; 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",null,"4; 6,3",null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,null,5,null,null,"2,5; 4; 5; 6,3"]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",null,"6,3; 8; 10",null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,null,9,null,null,"5; 6,3; 8; 10"]
[32,"10; 22","6,3; 10; 16",null,"10; 16",null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,null,15,null,null,"8; 10; 12,5; 16"]
[40,"10; 25","10; 16; 25",null,"16; 20; 25",30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,null,22,null,null,"12,5; 16; 20;25"]
[50,"10; 32","10; 16; 25; 32; 40",null,"25; 32; 40",null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,null,40,null,30,"20; 25; 31,5; 40"]
[65,32,"25; 32; 40; 63",40,"40; 50; 63",null,"40; 63","20; 38","16; 25; 40; 63",null,null,63,null,null,"31,5; 40; 50; 63"]
[80,40,"40; 63; 80; 100",null,"63; 80; 100",null,"63; 100",null,"25; 40; 63; 94",null,null,90,null,50,"50; 63; 80; 100"]
[100,50,"63; 80; 100; 125;160",null,"100; 125; 145",null,"100; 160",38,"94; 125; 160",null,null,136,null,null,"80; 100; 125; 160"]
[125,80,"100; 125; 160; 250",null,"125; 160",50,"160; 250",null,null,null,null,230,null,60,"125; 160; 200; 250"]
[150,80,"160; 250; 360",null,"280; 320",null,"250; 400",null,null,null,null,316,null,null,"200; 250; 315; 400"]
[200,80,"250; 360; 450; 630",null,"320; 450",65,630,null,null,null,null,555,null,null,"315; 400; 500; 630"]
[250,null,null,null,"400; 630",null,1000,null,null,null,null,null,null,80,"400; 500; 630; 800"]
[300,null,null,null,null,null,null,null,null,null,null,null,null,null,"630; 800; 1000; 1250"]
[400]
["Разгрузка","с ду 65",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 25-100",null,"Все диаметры",null,null,null,"Все диаметры"]
["КПСР ","Серия 210",null,"VFG 2 /VFG 21",null,"STEVI 440",null,"Тип ZH",null,"RV 21x",null,"Гранрег КМ127Ф",null,"CV225"]
[null,null,null,"VFGS 2",null,"STEVI 470/422",null,"Тип Z",null,null,null,null,null,"CV240S"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"CV240E"]
["Тех.характеристики"]
["ДУ max",400,null,250,null,250,null,250,null,400,null,100,null,300,null,150,null,150]
["Давление, бар",25,null,"16 - 25",null,"16-40",null,"10; 16; 25; 40",null,"16; 40",null,40,null,"16-40",null,"16; 25",null,16]
["t, °C, max",260,null,250,null,450,null,450,null,"300…500",null,300,null,200,null,150,null,"150; 220"]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv",null,null,"kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",15,"0,4;0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 4",null,null,4,null,20,"0,16; 0,25; 0,4 ;0,63; 1; 1,25; 1,6; 2,5; 4",15,"0,4; 0,63; 1; 1,6; 2,5;4",null,"0,16 - 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",null,"4; 6,3",null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,null,5,null,null,"2,5; 4; 5; 6,3",null,"4; 6,3",null,6.3]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",null,"6,3; 8; 10",null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,null,9,null,null,"5; 6,3; 8; 10",null,"6,3; 10",null,"5,0 - 10"]
[32,"10; 22","6,3; 10; 16",null,"10; 16",null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,null,15,null,null,"8; 10; 12,5; 16",null,"10; 16",null,16]
[40,"10; 25","10; 16; 25",null,"16; 20; 25",30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,null,22,null,null,"12,5; 16; 20;25",null,"16; 25",null,"12,5 - 25"]
[50,"10; 32","10; 16; 25; 32; 40",null,"25; 32; 40",null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,null,40,null,30,"20; 25; 31,5; 40",null,"25; 40",null,"31,5; 40"]
[65,32,"25; 32; 40; 63",40,"40; 50; 63",null,"40; 63","20; 38","16; 25; 40; 63",null,null,63,null,null,"31,5; 40; 50; 63","18; 30","58; 63",null,"50; 63"]
[80,40,"40; 63; 80; 100",null,"63; 80; 100",null,"63; 100",null,"25; 40; 63; 94",null,null,90,null,50,"50; 63; 80; 100",30,"90; 100",null,"80; 100"]
[100,50,"63; 80; 100; 125;160",null,"100; 125; 145",null,"100; 160",null,"40; 63; 94; 125; 160",null,null,136,null,null,"80; 100; 125; 160",null,"125; 145",null,"125; 160"]
[125,80,"100; 125; 160; 250",null,"125; 160",50,"160; 250",null,"40; 63; 94; 125; 160",null,null,null,null,60,"125; 160; 200; 250",40,200,null,"200; 250"]
[150,80,"160; 250; 360",null,"280; 320",null,"250; 400","38; 50"," 63; 94; 125; 160; 250; 320",null,null,null,null,null,"200; 250; 315; 400",null,320,null,"315; 360; 400"]
[200,80,"250; 360; 450; 630",null,"320; 450",65,630,"38; 50; 63","94; 125; 160; 250; 320; 500",null,null,null,null,null,"315; 400; 500; 630"]
[250,80,"400; 630; 800; 1000",null,"400; 630",null,1000,null,"125; 160; 250; 320; 500; 630",null,null,null,null,80,"400; 500; 630; 800"]
[300,100,"1000; 1250; 1600",null,null,null,null,null,null,null,null,null,null,null,"630; 800; 1000; 1250"]
[400,100,"1250; 1600; 2000; 2500"]
["Разгрузка","с ду 50",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 40-250",null,"Все диаметры",null,null,null,"Все диаметры",null,"Частично разгружены ду 65-100",null,"С компенсацией давления с ду 50"]
["КССР","Серия 100",null,"VF3",null,"STEVI 450",null,"Тип Z3",null,"RV 113 M",null,"Гранрег КМ 307Ф",null,"CV306/316 GG",null,"H7xxR",null,"VXF42xx"]
[null,null,null,null,null,null,null,null,null,null,null,"Гранрег КМ317Ф",null,"CV316",null,null,null,"VXF43xx"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"VXF53xx"]
["Тех.характеристики"]
["ДУ max",150,null,150,null,300,null,150,null,150,null,300,null,200,null,120,null,220]
["Давление, бар",16,null,16,null,"16-40",null,"16; 25; 40",null,"6; 16",null,16,null,"6; 16",null,6,null,"16; 25"]
["t, °C, max",150,null,200,null,150,null,450,null,150,null,230,null,300,null,100,null,150]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,10," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5;  4",15,"0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,63; 1; 1,6; 2,5; 4",20,"1,6; 2,5; 4",4,null,"14; 20","0,63; 1,25; 1,6; 2,5; 4",15,"0,63; 1; 1,6; 2,5;4",20,"1,6; 2,5; 4"]
[20,15,"1,6; 2,5; 4; 6,3",null,6.3,null," 4; 6,3",null,"0,63; 1; 1,6; 2,5; 4; 6,3",null,6.3,6.3,null,null,"2,5; 4; 5; 6,3",null,6.3,null,6.3]
[25,20,"1,6; 2,5; 4,0; 6,3;10",null,10,null,"6,3; 10",null,"0,63; 1; 1,6; 2,5; 4; 6,3; 10",null,10,10,null,null,"5; 6,3; 8; 10",null,10,null,"6,3; 10"]
[32,22,"6,3; 10; 16",null,16,null,"16; 10",null,"6,3; 10; 16",null,16,16,null,null,"8; 10; 12,5; 16",null,16,null,16]
[40,null,"10; 16; 25",null,25,null,"16; 25",null,"10; 16; 25",null,25,25,null,null,"12,5; 16; 20; 25",null,25,null,"16; 25"]
[50,25,"10; 16; 25; 40",null,40,null,"25; 40",null,"16; 25; 40",null,40,40,null,"14; 30","20; 25; 31,5; 40",null,40,null,"31,5; 40"]
[65,32,"25; 32; 40; 63",20,63,30,"40; 63","20; 38","25; 40; 63",null,63,63,null,"20; 30","31,5; 40; 50; 63",18,58,null,"50; 63"]
[80,null,"40; 63;100",30,100,null,"63; 100",null,"40; 63; 94",null,100,"70; 100",null,50,"50; 63; 80; 100",null,90,null,"80; 100"]
[100,null,"63; 80; 100; 125;160",null,145,null,"100; 160",38,"63; 94; 125; 160",40,160,"130; 160",null,null,"80; 100; 125;160",30,145,40,"125; 160"]
[125,null,"100; 125; 160; 250",40,220,50,"160; 250","38; 50","125; 160; 250; 320",null,250,"200; 230",null,60,"125; 160; 200; 250",null,null,null,"200; 250"]
[150,null,"160; 250; 360",null,320,null,"250; 320",null,null,null,360,"270; 340",null,null,"200; 250; 315; 400",null,null,null,"315; 400"]
[200,null,null,null,null,null,null,null,null,null,null,"600; 420",null,null,"315; 400; 500; 630"]
[250,null,null,null,null,null,null,null,null,null,null,"900; 640",null,80,"400; 500; 630; 800"]
[300,null,null,null,null,null,null,null,null,null,null,"1200; 930",null,null,"630; 800; 1000; 1250"]
[]
["РА","Серия 100",null,"VFG2 + AFD",null,"ARI-PREDU",null,"Тип ZSN1",null,"RD 122"]
[null,"Серия 200",null,"VFGS2 + AFD",null,null,null,"Тип ZSN3"]
[null,null,null," AVA",null,null,null,"Тип ZSN5"]
[null,null,null,"AVP",null,null,null,"Тип ZSN7"]
["Тех.характеристики"]
["ДУ max",200,null,250,null,150,null,150,null,50]
["Давление, бар","16 ; 25",null,"16-40",null,"16-40",null,"16; 25; 40",null,25]
["t, °C, max",220,null,350,null,350,null,200,null,150]
["kv","kv",null,"kv",null,"ход штока, max","kv","ход штока, max","kv","kv"]
[15," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",null,"1,6; 4; 2,5",null,4,"0,1; 0,4; 1; 2,5; 3,2",6,"1; 1,6; 2,5; 3,2","2,5; 5"]
[20,"1,6; 2,5; 4; 6,3",null,"6,3: 4",null,5,"0,1; 0,4; 1; 2,5; 4; 5",null,"1,6; 2,5; 3,2; 5",8]
[25,"1,6; 2,5; 4,0; 6,3; 8; 10",null,"8; 6,3",null,6,"0,1; 0,4; 1; 2,5; 4; 6,3; 8",null,"2,5; 3,2; 5; 8",10]
[32,"6,3; 10; 16",null,"12,5; 16; 10",null,8,12.5,8,"12,5; 5",15]
[40,"10; 16; 20; 25",null,"20; 16",null,8,20,null,"8; 20",21]
[50,"10; 16; 25; 32; 40",null,"32;25",null,10,32,null,"12,5; 32",32]
[65,"25; 40; 50; 63",null,"50; 40",null,11,50,12,"20; 50"]
[80,"40; 63; 80; 100",null,"80; 63",null,13,80,null,"32; 80"]
[100,"63; 100; 125",null,"125; 100",null,16,125,14,"50; 125"]
[125,"100; 125; 160",null,"160; 125",null,19,190,"спец. Исполнение, по индивид согласованию"]
[150,"160; 280",null,"280; 200",null,22,280]
[200,"250; 360; 450; 630",null,"320; 225"]
[250,null,null,"400; 280"]
[300]
[400]
[" Диапазон настройки, Мпа","0 - (0,01…0,1)",null,"(0,8…1,6)",null,"(0,2…0,6)",null,"(0,01…0,04)",null,"ду 15-25"]
[null,"1 - (0,04...0,16)",null,"(0,3…1,2)",null,"(0,5…1,2)",null,"(0,02…0,08)",null,"(0,015…0,06)"]
[null,"2 - (0,1…0,4)",null,"(0,1…0,6)",null,"(0,8…2,5)",null,"(0,04…0,16)",null,"(0,03…0,21)"]
[null,"3  - (0,3…0,7)",null,"(0,05…0,3)",null,"(2…5)",null,"(0,04…0,16)",null,"(0,06…0,4)"]
[null,"4 - (0,6…1,2)",null,"(0,01…0,07)",null,"(4,5…10)",null,"(0,08…0,32)",null,"ду 32-50"]
[null,null,null,"(0,015…0,15)",null,"(8…16)",null,"(0,1…0,4)",null,"(0,025…0,07)"]
[null,null,null,"(0,005…0,035)",null,null,null,"(0,2…0,8)",null,"(0,04…0,22)"]
[null,null,null,null,null,null,null,"(0,28…1,12)",null,"(0,07…0,41)"]

{"sheet":"КПСР 100,110","index":3,"n_rows":27,"n_cols":19,"rows_kept":27,"cut":false,"hidden":true,"merged":[[22,15,25,16],[22,17,25,18],[0,0,0,18],[26,13,26,14],[26,15,26,16],[26,17,26,18],[26,9,26,10],[24,3,25,4],[24,5,25,6],[20,7,25,8],[22,9,25,10],[23,11,25,12],[22,13,25,14],[22,5,23,5],[22,11,22,12],[26,1,26,2],[26,3,26,4],[26,5,26,6],[26,7,26,8],[26,11,26,12],[18,13,21,13],[18,15,19,15],[19,9,21,9],[19,11,19,12],[10,11,10,12],[11,5,14,5],[11,7,16,7],[11,9,18,9],[11,11,11,12],[11,13,16,13],[11,15,16,15],[11,17,18,17],[19,17,21,17],[20,5,21,5],[20,11,20,12],[20,15,21,15],[21,11,21,12],[12,11,12,12],[13,11,13,12],[14,11,14,12],[15,5,19,5],[15,11,15,12],[16,11,16,12],[17,7,18,7],[17,11,17,12],[18,11,18,12],[8,13,8,14],[8,15,8,16],[8,17,8,18],[9,1,9,2],[9,3,9,4],[9,5,9,6],[9,7,9,8],[9,9,9,10],[9,11,9,12],[9,13,9,14],[8,1,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,9,8,10],[8,11,8,12],[9,15,9,16],[9,17,9,18],[5,15,5,16],[5,17,5,18],[6,0,6,18],[7,1,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,9,7,10],[7,11,7,12],[7,13,7,14],[7,15,7,16],[7,17,7,18],[1,0,5,0],[5,1,5,2],[5,3,5,4],[5,5,5,6],[5,7,5,8],[5,9,5,10],[5,11,5,12],[5,13,5,14],[3,17,3,18],[4,1,4,2],[4,3,4,4],[4,5,4,6],[4,7,4,8],[4,9,4,10],[4,11,4,12],[4,13,4,14],[4,15,4,16],[4,17,4,18],[3,1,3,2],[3,3,3,4],[3,5,3,6],[3,7,3,8],[3,9,3,10],[3,11,3,12],[3,13,3,14],[3,15,3,16],[1,17,1,18],[2,1,2,2],[2,3,2,4],[2,5,2,6],[2,7,2,8],[2,9,2,10],[2,11,2,12],[2,13,2,14],[2,15,2,16],[2,17,2,18],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8],[1,9,1,10],[1,11,1,12],[1,13,1,14],[1,15,1,16]]}
["Клапаны запорно-регулирующие двухходовые, серия 100,110"]
["КПСР ","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM",null,"ADL",null,"TA",null,"Belimo",null,"Siemens"]
[null,"Серия 100 ",null,"VB 2",null,"STEVI 440",null,"Тип ZH",null,"RV 122",null,"Гранрег КМ125Ф",null,"CV206/216 GG",null,"H6xxN",null,"VVF42xx"]
[null,"Серия 110",null,"VFM 2",null,"STEVI 470/422",null,null,null,"RV 113 R",null,null,null,"CV216",null,"H6xxS",null,"VVF43xx"]
[null,null,null,"VF 2",null,null,null,null,null,"RV 2xx",null,null,null,null,null,"H6xxSP",null,"VVF53xx"]
[null,null,null,"VFG 2 /VFG 21"]
["Тех.характеристики"]
["ДУ max",400,null,250,null,250,null,100,null,150,null,200,null,150,null,150,null,150]
["Давление, бар","16 - 25",null,40,null,"16-40",null,"16-40",null,"6; 16; 25",null,16,null,"6; 16",null,"16; 25",null,16]
["t, °C, max",150,null,200,null,450,null,260,null,150,null,200,null,150,null,150,null,"150; 220"]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv 0,16..40","kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",5,"0,25; 0,4; 0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4",20,"1,6; 2,5; 4",4,null,14,"0,63; 1,25; 1,6; 2,5; 4",15,"0,4; 0,63; 1; 1,6; 2,5;4",20,"0,16 - 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",5,6.3,null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,6.3,5,null,null,"5; 6,3",null,"4; 6,3",null,6.3]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",7,10,null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,10,9,null,null,"8; 10",null,"6,3; 10",null,"5,0 - 10"]
[32,"10; 22","6,3; 10; 16",10,16,null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,16,15,null,null,"12,5; 16",null,"10; 16",null,16]
[40,"10; 25","10; 16; 25",10,25,30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,25,22,null,null,"20; 25",null,"16; 25",null,"12,5 - 25"]
[50,"10; 32","10; 16; 25; 32; 40",10,40,null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,40,40,null,null,"31,5; 40",null,"25; 40",null,"31,5; 40"]
[65,32,"25; 32; 40; 63",20,63,null,"40; 63","20; 38","16; 25; 40; 63",null,63,63,null,"20; 30","50; 63","18; 30","58; 63",null,"50; 63"]
[80,40,"40; 63; 80; 100",30,100,null,"63; 100",null,"25; 40; 63; 94",null,100,90,null,50,"80; 100",30,"90; 100",null,"80; 100"]
[100,50,"63; 80; 100; 125;160",30,160,null,"100; 160",38,"94; 125; 160",40,160,136,null,null,"125;160",null,"125; 145",40,"125; 160"]
[125,80,"100; 125; 160; 250",40,250,50,"160; 250",null,null,null,250,230,null,null,250,40,200,null,"200; 250"]
[150,80,"160; 250; 360",40,400,null,"250; 400",null,null,null,360,316,null,null,315,null,320,null,"315; 360; 400"]
[200,80,"250; 360; 450; 630",24,630,65,630,null,null,null,null,555]
[250,80,"400; 630; 800; 1000",24,900,null,1000]
[300,100,"1000; 1250; 1600"]
[400,100,"1250; 1600; 2000; 2500"]
["Разгрузка","Все диаметры",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 25-100",null,"Все диаметры",null,null,null,"Все диаметры",null,"Частично разгружены ду 65-100",null,"С компенсацией давления с ду 50"]

{"sheet":"КПСР 200","index":4,"n_rows":26,"n_cols":15,"rows_kept":26,"cut":false,"hidden":true,"merged":[[0,0,0,14],[25,13,25,14],[24,17,24,18],[1,0,4,0],[22,1,24,2],[23,3,24,4],[23,5,24,6],[19,7,24,8],[22,11,24,12],[24,13,24,14],[25,1,25,2],[25,3,25,4],[25,5,25,6],[25,7,25,8],[25,9,25,10],[25,11,25,12],[19,5,20,5],[19,11,19,12],[19,13,21,13],[18,15,19,15],[20,11,20,12],[21,5,22,5],[21,11,21,12],[22,13,23,13],[16,3,18,3],[16,7,17,7],[16,11,16,12],[17,11,17,12],[17,13,18,13],[16,15,17,15],[18,11,18,12],[12,11,12,12],[13,11,13,12],[14,5,18,5],[14,11,14,12],[15,11,15,12],[15,13,16,13],[7,15,7,16],[7,17,7,18],[9,11,9,12],[10,3,15,3],[10,5,13,5],[10,7,15,7],[10,11,10,12],[10,13,14,13],[9,15,14,15],[11,11,11,12],[7,13,7,14],[8,1,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,9,8,10],[8,11,8,12],[8,13,8,14],[7,1,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,9,7,10],[7,11,7,12],[4,17,4,18],[6,1,6,2],[6,3,6,4],[6,5,6,6],[6,7,6,8],[6,9,6,10],[6,11,6,12],[6,13,6,14],[5,15,5,16],[5,17,5,18],[4,7,4,8],[4,9,4,10],[4,11,4,12],[4,13,4,14],[5,0,5,14],[4,15,4,16],[6,15,6,16],[6,17,6,18],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8],[1,9,1,10],[1,11,1,12],[1,13,1,14],[2,13,2,14],[3,1,3,2],[3,3,3,4],[3,5,4,6],[3,7,3,8],[3,9,3,10],[3,11,3,12],[3,13,3,14],[4,1,4,2],[4,3,4,4],[2,1,2,2],[2,3,2,4],[2,5,2,6],[2,7,2,8],[2,9,2,10],[2,11,2,12]]}
["Клапаны запорно-регулирующие двухходовые, серия 200"]
["КПСР ","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM",null,"ADL",null,"TA"]
[null,"Серия 200",null,"VFS 2",null,"STEVI 440",null,"Тип ZH",null,"RV 21x",null,"Гранрег КМ125Ф",null,"CV225"]
[null,null,null,"VEFS 2",null,"STEVI 470/422"]
[null,null,null,"VFGS 2"]
["Тех.характеристики"]
["ДУ max",200,null,250,null,250,null,100,null,400,null,200,null,300]
["Давление, бар",25,null,25,null,"16-40",null,"16-40",null,"16; 40",null,16,null,"16-40"]
["t, °C, max",220,null,250,null,450,null,260,null,"300…500",null,200,null,200]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","kv",null,"ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",15,"0,4;0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4",null,null,4,null,20,"0,16; 0,25; 0,4 ;0,63; 1; 1,25; 1,6; 2,5; 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",null,"4; 6,3",null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,null,5,null,null,"2,5; 4; 5; 6,3"]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",null,"6,3; 8; 10",null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,null,9,null,null,"5; 6,3; 8; 10"]
[32,"10; 22","6,3; 10; 16",null,"10; 16",null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,null,15,null,null,"8; 10; 12,5; 16"]
[40,"10; 25","10; 16; 25",null,"16; 20; 25",30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,null,22,null,null,"12,5; 16; 20;25"]
[50,"10; 32","10; 16; 25; 32; 40",null,"25; 32; 40",null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,null,40,null,30,"20; 25; 31,5; 40"]
[65,32,"25; 32; 40; 63",40,"40; 50; 63",null,"40; 63","20; 38","16; 25; 40; 63",null,null,63,null,null,"31,5; 40; 50; 63"]
[80,40,"40; 63; 80; 100",null,"63; 80; 100",null,"63; 100",null,"25; 40; 63; 94",null,null,90,null,50,"50; 63; 80; 100"]
[100,50,"63; 80; 100; 125;160",null,"100; 125; 145",null,"100; 160",38,"94; 125; 160",null,null,136,null,null,"80; 100; 125; 160"]
[125,80,"100; 125; 160; 250",null,"125; 160",50,"160; 250",null,null,null,null,230,null,60,"125; 160; 200; 250"]
[150,80,"160; 250; 360",null,"280; 320",null,"250; 400",null,null,null,null,316,null,null,"200; 250; 315; 400"]
[200,80,"250; 360; 450; 630",null,"320; 450",65,630,null,null,null,null,555,null,null,"315; 400; 500; 630"]
[250,null,null,null,"400; 630",null,1000,null,null,null,null,null,null,80,"400; 500; 630; 800"]
[300,null,null,null,null,null,null,null,null,null,null,null,null,null,"630; 800; 1000; 1250"]
[400]
["Разгрузка","с ду 65",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 25-100",null,"Все диаметры",null,null,null,"Все диаметры"]

{"sheet":"КПСР 210","index":5,"n_rows":26,"n_cols":19,"rows_kept":26,"cut":false,"hidden":true,"merged":[[0,0,0,18],[8,9,8,10],[25,9,25,10],[19,11,24,12],[24,13,24,14],[21,15,24,16],[21,17,24,18],[25,15,25,16],[25,13,25,14],[25,17,25,18],[1,15,1,16],[1,17,1,18],[2,15,2,16],[2,17,2,18],[3,15,3,16],[3,17,3,18],[4,15,4,16],[4,17,4,18],[25,1,25,2],[25,3,25,4],[25,5,25,6],[25,7,25,8],[25,11,25,12],[23,3,24,4],[19,15,20,15],[21,5,22,5],[21,7,22,7],[22,13,23,13],[16,3,18,3],[16,7,19,7],[16,11,16,12],[17,11,17,12],[17,13,18,13],[17,15,18,15],[18,11,18,12],[19,5,20,5],[19,13,21,13],[12,11,12,12],[13,11,13,12],[14,5,18,5],[14,11,14,12],[15,11,15,12],[15,13,16,13],[9,11,9,12],[23,5,24,6],[23,7,24,8],[10,3,15,3],[10,5,13,5],[10,7,15,7],[10,11,10,12],[10,13,14,13],[7,15,7,16],[7,17,7,18],[8,1,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,11,8,12],[8,13,8,14],[8,15,8,16],[8,17,8,18],[7,1,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,11,7,12],[7,13,7,14],[7,9,7,10],[10,15,15,15],[11,11,11,12],[5,0,5,18],[6,1,6,2],[6,3,6,4],[6,5,6,6],[6,7,6,8],[6,11,6,12],[6,13,6,14],[6,15,6,16],[6,17,6,18],[6,9,6,10],[3,13,3,14],[4,9,4,10],[4,13,4,14],[1,11,1,12],[1,13,1,14],[2,1,2,2],[2,3,2,4],[2,5,2,6],[2,7,2,8],[2,9,2,10],[2,11,2,12],[2,13,2,14],[1,0,4,0],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8],[1,9,1,10],[3,3,3,4],[3,5,4,6],[3,7,3,8],[3,9,3,10]]}
["Клапаны запорно-регулирующие двухходовые, серия 210"]
["КПСР ","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM",null,"ADL",null,"TA",null,"Belimo",null,"Siemens"]
[null,"Серия 210",null,"VFG 2 /VFG 21",null,"STEVI 440",null,"Тип ZH",null,"RV 21x",null,"Гранрег КМ127Ф",null,"CV225",null,"H6xxN",null,"VVF42xx"]
[null,null,null,"VFGS 2",null,"STEVI 470/422",null,"Тип Z",null,null,null,null,null,"CV240S",null,"H6xxS",null,"VVF43xx"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"CV240E",null,"H6xxSP",null,"VVF53xx"]
["Тех.характеристики"]
["ДУ max",400,null,250,null,250,null,250,null,400,null,100,null,300,null,150,null,150]
["Давление, бар",25,null,"16 - 25",null,"16-40",null,"10; 16; 25; 40",null,"16; 40",null,40,null,"16-40",null,"16; 25",null,16]
["t, °C, max",260,null,250,null,450,null,450,null,"300…500",null,300,null,200,null,150,null,"150; 220"]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv",null,null,"kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,"5; 10"," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",15,"0,4;0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 4",null,null,4,null,20,"0,16; 0,25; 0,4 ;0,63; 1; 1,25; 1,6; 2,5; 4",15,"0,4; 0,63; 1; 1,6; 2,5;4",null,"0,16 - 4"]
[20,"5; 10","1,6; 2,5; 4; 6,3",null,"4; 6,3",null,"2,5; 4; 6,3",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3",null,null,5,null,null,"2,5; 4; 5; 6,3",null,"4; 6,3",null,6.3]
[25,"7; 20","1,6; 2,5; 4,0; 6,3;10",null,"6,3; 8; 10",null,"6,3; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10",null,null,9,null,null,"5; 6,3; 8; 10",null,"6,3; 10",null,"5,0 - 10"]
[32,"10; 22","6,3; 10; 16",null,"10; 16",null,"16; 10",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16",null,null,15,null,null,"8; 10; 12,5; 16",null,"10; 16",null,16]
[40,"10; 25","10; 16; 25",null,"16; 20; 25",30,"16; 25",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25",null,null,22,null,null,"12,5; 16; 20;25",null,"16; 25",null,"12,5 - 25"]
[50,"10; 32","10; 16; 25; 32; 40",null,"25; 32; 40",null,"25; 40",null,"0,01; 0,016; 0,025; 0,04; 0,063; 0,1; 0,16; 0,25; ,04; 0,63,; 1; 1,6; 2,5; 4; 6,3; 10; 16; 25; 40",null,null,40,null,30,"20; 25; 31,5; 40",null,"25; 40",null,"31,5; 40"]
[65,32,"25; 32; 40; 63",40,"40; 50; 63",null,"40; 63","20; 38","16; 25; 40; 63",null,null,63,null,null,"31,5; 40; 50; 63","18; 30","58; 63",null,"50; 63"]
[80,40,"40; 63; 80; 100",null,"63; 80; 100",null,"63; 100",null,"25; 40; 63; 94",null,null,90,null,50,"50; 63; 80; 100",30,"90; 100",null,"80; 100"]
[100,50,"63; 80; 100; 125;160",null,"100; 125; 145",null,"100; 160",null,"40; 63; 94; 125; 160",null,null,136,null,null,"80; 100; 125; 160",null,"125; 145",null,"125; 160"]
[125,80,"100; 125; 160; 250",null,"125; 160",50,"160; 250",null,"40; 63; 94; 125; 160",null,null,null,null,60,"125; 160; 200; 250",40,200,null,"200; 250"]
[150,80,"160; 250; 360",null,"280; 320",null,"250; 400","38; 50"," 63; 94; 125; 160; 250; 320",null,null,null,null,null,"200; 250; 315; 400",null,320,null,"315; 360; 400"]
[200,80,"250; 360; 450; 630",null,"320; 450",65,630,"38; 50; 63","94; 125; 160; 250; 320; 500",null,null,null,null,null,"315; 400; 500; 630"]
[250,80,"400; 630; 800; 1000",null,"400; 630",null,1000,null,"125; 160; 250; 320; 500; 630",null,null,null,null,80,"400; 500; 630; 800"]
[300,100,"1000; 1250; 1600",null,null,null,null,null,null,null,null,null,null,null,"630; 800; 1000; 1250"]
[400,100,"1250; 1600; 2000; 2500"]
["Разгрузка","с ду 50",null,"Все диаметры",null,"Все диаметры",null,"Разгружены ду 40-250",null,"Все диаметры",null,null,null,"Все диаметры",null,"частично разгружены ду 65-100",null,"С компенсацией давления с ду 50"]

{"sheet":"КССР","index":6,"n_rows":24,"n_cols":19,"rows_kept":24,"cut":false,"hidden":true,"merged":[[24,13,24,14],[19,15,24,16],[21,17,24,18],[0,0,0,18],[24,11,24,12],[21,1,24,2],[21,3,24,4],[21,5,24,6],[20,7,24,8],[21,9,24,10],[21,11,21,12],[22,11,22,12],[22,13,23,13],[23,11,23,12],[18,17,20,17],[19,1,20,1],[13,11,13,12],[14,11,14,12],[15,11,15,12],[16,15,17,15],[17,3,18,3],[17,11,17,12],[17,13,18,13],[18,9,20,9],[18,11,18,12],[19,3,20,3],[19,5,20,5],[19,11,19,12],[19,13,21,13],[20,11,20,12],[16,1,17,1],[16,5,18,5],[16,7,17,7],[16,11,16,12],[8,17,8,18],[9,11,9,12],[10,3,15,3],[10,5,15,5],[10,7,15,7],[10,9,17,9],[10,11,10,12],[10,13,14,13],[10,17,17,17],[11,11,11,12],[12,11,12,12],[13,1,14,1],[7,15,7,16],[7,17,7,18],[8,1,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,9,8,10],[8,11,8,12],[8,13,8,14],[8,15,8,16],[6,13,6,14],[6,15,6,16],[6,17,6,18],[7,1,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,9,7,10],[7,11,7,12],[7,13,7,14],[6,1,6,2],[6,3,6,4],[6,5,6,6],[6,7,6,8],[6,9,6,10],[6,11,6,12],[1,9,1,10],[4,17,4,18],[3,17,3,18],[4,5,4,6],[4,9,4,10],[2,13,2,14],[2,15,2,16],[2,17,2,18],[3,5,3,6],[3,9,3,10],[3,11,3,12],[3,13,3,14],[1,0,4,0],[5,0,5,18],[1,11,1,12],[1,13,1,14],[1,15,1,16],[1,17,1,18],[2,1,2,2],[2,3,2,4],[2,5,2,6],[2,7,2,8],[2,9,2,10],[2,11,2,12],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8]]}
["Клапаны смесительные трехходовые"]
["КССР","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM",null,"ADL",null,"TA",null,"Belimo",null,"Siemens"]
[null,"Серия 100",null,"VF3",null,"STEVI 450",null,"Тип Z3",null,"RV 113 M",null,"Гранрег КМ 307Ф",null,"CV306/316 GG",null,"H7xxR",null,"VXF42xx"]
[null,null,null,null,null,null,null,null,null,null,null,"Гранрег КМ317Ф",null,"CV316",null,null,null,"VXF43xx"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"VXF53xx"]
["Тех.характеристики"]
["ДУ max",150,null,150,null,300,null,150,null,150,null,300,null,200,null,120,null,220]
["Давление, бар",16,null,16,null,"16-40",null,"16; 25; 40",null,"6; 16",null,16,null,"6; 16",null,6,null,"16; 25"]
["t, °C, max",150,null,200,null,150,null,450,null,150,null,230,null,300,null,100,null,150]
["ход штока/kv","ход штока","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","ход штока, max","kv","kv",null,"ход штока, max","kv","ход штока, max","kv","ход штока, max","kv"]
[15,10," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5;  4",15,"0,63; 1; 1,6; 2,5; 4",20,"2,5; 4",20,"0,63; 1; 1,6; 2,5; 4",20,"1,6; 2,5; 4",4,null,"14; 20","0,63; 1,25; 1,6; 2,5; 4",15,"0,63; 1; 1,6; 2,5;4",20,"1,6; 2,5; 4"]
[20,15,"1,6; 2,5; 4; 6,3",null,6.3,null," 4; 6,3",null,"0,63; 1; 1,6; 2,5; 4; 6,3",null,6.3,6.3,null,null,"2,5; 4; 5; 6,3",null,6.3,null,6.3]
[25,20,"1,6; 2,5; 4,0; 6,3;10",null,10,null,"6,3; 10",null,"0,63; 1; 1,6; 2,5; 4; 6,3; 10",null,10,10,null,null,"5; 6,3; 8; 10",null,10,null,"6,3; 10"]
[32,22,"6,3; 10; 16",null,16,null,"16; 10",null,"6,3; 10; 16",null,16,16,null,null,"8; 10; 12,5; 16",null,16,null,16]
[40,null,"10; 16; 25",null,25,null,"16; 25",null,"10; 16; 25",null,25,25,null,null,"12,5; 16; 20; 25",null,25,null,"16; 25"]
[50,25,"10; 16; 25; 40",null,40,null,"25; 40",null,"16; 25; 40",null,40,40,null,"14; 30","20; 25; 31,5; 40",null,40,null,"31,5; 40"]
[65,32,"25; 32; 40; 63",20,63,30,"40; 63","20; 38","25; 40; 63",null,63,63,null,"20; 30","31,5; 40; 50; 63",18,58,null,"50; 63"]
[80,null,"40; 63;100",30,100,null,"63; 100",null,"40; 63; 94",null,100,"70; 100",null,50,"50; 63; 80; 100",null,90,null,"80; 100"]
[100,null,"63; 80; 100; 125;160",null,145,null,"100; 160",38,"63; 94; 125; 160",40,160,"130; 160",null,null,"80; 100; 125;160",30,145,40,"125; 160"]
[125,null,"100; 125; 160; 250",40,220,50,"160; 250","38; 50","125; 160; 250; 320",null,250,"200; 230",null,60,"125; 160; 200; 250",null,null,null,"200; 250"]
[150,null,"160; 250; 360",null,320,null,"250; 320",null,null,null,360,"270; 340",null,null,"200; 250; 315; 400",null,null,null,"315; 400"]
[200,null,null,null,null,null,null,null,null,null,null,"600; 420",null,null,"315; 400; 500; 630"]
[250,null,null,null,null,null,null,null,null,null,null,"900; 640",null,80,"400; 500; 630; 800"]
[300,null,null,null,null,null,null,null,null,null,null,"1200; 930",null,null,"630; 800; 1000; 1250"]

{"sheet":"РА 100,200","index":7,"n_rows":34,"n_cols":10,"rows_kept":34,"cut":false,"hidden":true,"merged":[[33,5,33,6],[0,0,0,10],[33,1,33,2],[33,3,33,4],[33,7,33,8],[33,9,33,10],[17,9,25,10],[22,7,25,8],[22,5,25,6],[31,1,31,2],[31,3,31,4],[31,5,31,6],[31,7,31,8],[31,9,31,10],[32,1,32,2],[32,3,32,4],[32,7,32,8],[32,9,32,10],[32,5,32,6],[29,1,29,2],[29,3,29,4],[29,5,29,6],[29,7,29,8],[29,9,29,10],[26,0,30,0],[26,1,26,2],[26,3,26,4],[26,5,26,6],[26,7,26,8],[26,9,26,10],[27,1,27,2],[27,3,27,4],[27,5,27,6],[27,7,27,8],[30,1,30,2],[30,3,30,4],[30,5,30,6],[30,7,30,8],[30,9,30,10],[27,9,27,10],[28,1,28,2],[28,3,28,4],[28,5,28,6],[28,7,28,8],[28,9,28,10],[24,3,25,4],[23,1,25,2],[22,1,22,2],[22,3,22,4],[23,3,23,4],[19,1,19,2],[19,3,19,4],[20,1,20,2],[20,3,20,4],[14,1,14,2],[14,3,14,4],[14,7,16,7],[14,9,14,10],[15,1,15,2],[15,3,15,4],[15,9,15,10],[20,7,21,8],[21,1,21,2],[21,3,21,4],[16,1,16,2],[16,3,16,4],[16,9,16,10],[17,1,17,2],[17,3,17,4],[17,7,18,7],[18,1,18,2],[18,3,18,4],[10,1,10,2],[10,3,10,4],[10,9,10,10],[11,1,11,2],[11,3,11,4],[11,7,13,7],[11,9,11,10],[12,1,12,2],[12,3,12,4],[12,9,12,10],[13,1,13,2],[13,3,13,4],[13,9,13,10],[8,1,8,2],[8,3,8,4],[8,5,8,6],[8,7,8,8],[8,9,8,10],[9,1,9,2],[9,3,9,4],[9,5,9,6],[9,7,9,8],[9,9,9,10],[6,0,6,10],[7,1,7,2],[7,3,7,4],[7,5,7,6],[7,7,7,8],[7,9,7,10],[4,3,4,4],[4,5,4,6],[4,7,4,8],[5,3,5,4],[5,5,5,6],[5,7,5,8],[3,1,3,2],[3,3,3,4],[3,5,3,6],[3,7,3,8],[2,9,5,10],[1,0,5,0],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8],[1,9,1,10],[2,1,2,2],[2,3,2,4],[2,5,2,6],[2,7,2,8]]}
["Регуляторы давления"]
["РА","КПСР Групп",null,"Danfoss",null,"Ari Armaturen",null,"POLNA",null,"LDM"]
[null,"Серия 100",null,"VFG2 + AFD",null,"ARI-PREDU",null,"Тип ZSN1",null,"RD 122"]
[null,"Серия 200",null,"VFGS2 + AFD",null,null,null,"Тип ZSN3"]
[null,null,null," AVA",null,null,null,"Тип ZSN5"]
[null,null,null,"AVP",null,null,null,"Тип ZSN7"]
["Тех.характеристики"]
["ДУ max",200,null,250,null,150,null,150,null,50]
["Давление, бар","16 ; 25",null,"16-40",null,"16-40",null,"16; 25; 40",null,25]
["t, °C, max",220,null,350,null,350,null,200,null,150]
["kv","kv",null,"kv",null,"ход штока, max","kv","ход штока, max","kv","kv"]
[15," 0,16; 0,25; 0,4; 0,63; 1; 1,6; 2,5; 3,2; 4",null,"1,6; 4; 2,5",null,4,"0,1; 0,4; 1; 2,5; 3,2",6,"1; 1,6; 2,5; 3,2","2,5; 5"]
[20,"1,6; 2,5; 4; 6,3",null,"6,3: 4",null,5,"0,1; 0,4; 1; 2,5; 4; 5",null,"1,6; 2,5; 3,2; 5",8]
[25,"1,6; 2,5; 4,0; 6,3; 8; 10",null,"8; 6,3",null,6,"0,1; 0,4; 1; 2,5; 4; 6,3; 8",null,"2,5; 3,2; 5; 8",10]
[32,"6,3; 10; 16",null,"12,5; 16; 10",null,8,12.5,8,"12,5; 5",15]
[40,"10; 16; 20; 25",null,"20; 16",null,8,20,null,"8; 20",21]
[50,"10; 16; 25; 32; 40",null,"32;25",null,10,32,null,"12,5; 32",32]
[65,"25; 40; 50; 63",null,"50; 40",null,11,50,12,"20; 50"]
[80,"40; 63; 80; 100",null,"80; 63",null,13,80,null,"32; 80"]
[100,"63; 100; 125",null,"125; 100",null,16,125,14,"50; 125"]
[125,"100; 125; 160",null,"160; 125",null,19,190,"спец. Исполнение, по индивид согласованию"]
[150,"160; 280",null,"280; 200",null,22,280]
[200,"250; 360; 450; 630",null,"320; 225"]
[250,null,null,"400; 280"]
[300]
[400]
[" Диапазон настройки, Мпа","0 - (0,01…0,1)",null,"(0,8…1,6)",null,"(0,2…0,6)",null,"(0,01…0,04)",null,"ду 15-25"]
[null,"1 - (0,04...0,16)",null,"(0,3…1,2)",null,"(0,5…1,2)",null,"(0,02…0,08)",null,"(0,015…0,06)"]
[null,"2 - (0,1…0,4)",null,"(0,1…0,6)",null,"(0,8…2,5)",null,"(0,04…0,16)",null,"(0,03…0,21)"]
[null,"3  - (0,3…0,7)",null,"(0,05…0,3)",null,"(2…5)",null,"(0,04…0,16)",null,"(0,06…0,4)"]
[null,"4 - (0,6…1,2)",null,"(0,01…0,07)",null,"(4,5…10)",null,"(0,08…0,32)",null,"ду 32-50"]
[null,null,null,"(0,015…0,15)",null,"(8…16)",null,"(0,1…0,4)",null,"(0,025…0,07)"]
[null,null,null,"(0,005…0,035)",null,null,null,"(0,2…0,8)",null,"(0,04…0,22)"]
[null,null,null,null,null,null,null,"(0,28…1,12)",null,"(0,07…0,41)"]

{"sheet":"Серия 110-VB2","index":8,"n_rows":49,"n_cols":21,"rows_kept":49,"cut":false,"hidden":false,"merged":[[46,1,46,22],[47,1,47,22],[48,1,48,22],[29,4,29,5],[23,15,23,20],[12,3,13,8],[15,3,15,8],[1,8,1,13],[2,8,2,13],[3,8,3,13],[15,15,15,20],[12,15,13,20]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VB 2 (VFM2 c 01.06.2016)",null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 110"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Для внутренних сетей и ИТП"]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))",null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,"Высокопрочный чугун (EN-JS 1025)"]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С",null,null,null,"max +150°С"]
[]
[]
[null,null,null,"DN, мм",null,null,null,null,null,null,null,null,null,null,null,"DN, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,null,null,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.25,6.3,10,16,25,40,null,null,null,null,null,null,0.25,6.3,10,16,25,40]
[null,null,null,0.4,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,0.63,null,null,null,null,null,null,null,null,null,null,null,0.63]
[null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5,2.5,10,16,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,null,20,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.3,null,null,32]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
[null,null,null,null,"Артикул"]
["Производитель","Изделие","DN","Kvs, м³/ч","VB2","VFM2",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VB2 (VFM2)",15,0.25,"065B2050","065B3050",null,"КПСР",null,null,"1-1-15-0,25-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,0.4,"065B2051","065B3051",null,"КПСР",null,null,"1-1-15-0,4-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,0.63,"065B2052","065B3052",null,"КПСР",null,null,"1-1-15-0,63-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,1,"065B2053","065B3053",null,"КПСР",null,null,"1-1-15-1-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,1.6,"065B2054","065B3054",null,"КПСР",null,null,"1-1-15-1,6-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,2.5,"065B2055","065B3055",null,"КПСР",null,null,"1-1-15-2,5-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",15,4,"065B2056","065B3056",null,"КПСР",null,null,"1-1-15-4-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VB2 (VFM2)",20,6.3,"065B2057","065B3057",null,"КПСР",null,null,"1-1-20-6,3-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VB2 (VFM2)",25,10,"065B2058","065B3058",null,"КПСР",null,null,"1-1-25-10-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",32,16,"065B2059","065B3059",null,"КПСР",null,null,"1-1-32-16-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",40,25,"065B2060","065B3060",null,"КПСР",null,null,"1-1-40-25-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VB2 (VFM2)",50,40,"065B2061","065B3061",null,"КПСР",null,null,"1-1-50-40-1.3501-СЧ-1,6-1-150-У"]
[]
[]
[]
[null,"По вопросам продаж и поддержки обращайтесь:"]
[]
[null,"Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFM2","index":9,"n_rows":40,"n_cols":21,"rows_kept":40,"cut":false,"hidden":false,"merged":[[37,0,37,21],[38,0,38,21],[39,0,39,21],[16,14,16,20],[11,3,12,9],[11,14,12,20],[1,8,1,13],[2,8,2,13],[3,8,3,13],[14,14,14,20],[14,3,14,9]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFM2",null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 100"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,65,80,100,125,150,200,250,null,null,null,null,65,80,100,125,150,200,250]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,63,100,160,250,400,630,900,null,null,null,null,63,"100","160","250","400","630","1000"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16","40","63",100,160,250,"400"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"25","63",80,"125","250","360",630]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,32,80,"100","160","360","460","800"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"40",null,"125","200"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"50"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"80"]
[]
[null,null,"Применяемость приводов к конкретному диаметру уточняйте у сотрудников компании"]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFM2",65,63,"065В3500",null,"КПСР",null,"1-1-65-63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFM2",80,100,"065В3501",null,"КПСР",null,"1-1-80-100-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFM2",100,160,"065В3502",null,"КПСР",null,"1-1-100-160-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFM2",125,250,"065В3503",null,"КПСР",null,"1-1-125-250-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFM2",150,400,"065В3504",null,"КПСР",null,"1-1-150-360-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFM2",200,630,"065В3505",null,"КПСР",null,"1-1-200-630-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFM2",250,900,"065В3506",null,"КПСР",null,"1-1-250-1000-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VL2","index":10,"n_rows":48,"n_cols":25,"rows_kept":48,"cut":false,"hidden":false,"merged":[[45,0,45,24],[46,0,46,24],[47,0,47,24],[14,16,14,24],[14,3,14,11],[20,16,20,24],[1,10,1,15],[2,10,2,15],[3,10,3,15],[11,16,12,24],[11,3,12,11]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапана Danfoss серии VL2",null,null,null,null,null,null,null,null,null,null,null,null,"Клапана КПСР серии 100"]
[]
["Рабочее давление",null,null,"0,6 МПа (6 атм)",null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +120°С",null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,null,null,null,null,15,20,25,32,40,50,65,80,100]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"0,63",6.3,10,16,25,40,63,100,145,null,null,null,null,0.63,6.3,"10",16,25,40,63,"100","160"]
[null,null,null,"1",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,"2,5",null,null,null,null,null,null,null,null,null,null,null,null,"2,5"]
[null,null,null,"4",null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,12.5,"25","63",80]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,20,16,32,80,"100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,10,6.3,null,25,25,"40",null,"125"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8,null,null,32,"50"]
[]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VL2",15,"0,63","065Z0371",null,"КПСР",null,"1-1-15-0,63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",15,"1","065Z0372",null,"КПСР",null,"1-1-15-1-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",15,"1,6","065Z0373",null,"КПСР",null,"1-1-15-1,6-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",15,"2,5","065Z0374",null,"КПСР",null,"1-1-15-2,5-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",15,"4","065Z0375",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VL2",20,"6,3","065Z0376",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VL2",25,"10","065Z0377",null,"КПСР",null,"1-1-25-10-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",32,"16","065Z0378",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",40,"25","065Z0379",null,"КПСР",null,"1-1-40-25-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",50,"40","065Z0380",null,"КПСР",null,"1-1-50-40-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",65,"63","065Z0381",null,"КПСР",null,"1-1-65-63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",80,"100","065Z0382",null,"КПСР",null,"1-1-80-100-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL2",100,"145","065Z3426",null,"КПСР",null,"1-1-100-145-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFS2","index":11,"n_rows":50,"n_cols":25,"rows_kept":50,"cut":false,"hidden":false,"merged":[[47,0,47,24],[48,0,48,24],[49,0,49,24],[14,16,14,24],[14,3,14,11],[21,16,21,24],[1,10,1,15],[2,10,2,15],[3,10,3,15],[11,16,12,24],[11,3,12,11]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFS2",null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 200"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))",null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)"]
["Рабочая температура",null,null,"max +200°С",null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +220°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,null,null,null,null,15,20,25,32,40,50,65,80,100]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.4,6.3,10,16,25,40,63,100,145,null,null,null,null,0.4,6.3,"10",16,25,40,63,"100","160"]
[null,null,null,"0,63",null,null,null,null,null,null,null,null,null,null,null,null,0.63]
[null,null,null,"1",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,"2,5",null,null,null,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,"4",null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,4,4,null,null,25,32,80,"100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.3,null,null,32,"40",null,"125"]
[]
[]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFS2",15,"0,4","065B1510",null,"КПСР",null,"1-1-15-0,4-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",15,"0,63","065B1511",null,"КПСР",null,"1-1-15-0,63-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",15,"1","065B1512",null,"КПСР",null,"1-1-15-1-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",15,"1,6","065B1513",null,"КПСР",null,"1-1-15-1,6-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFS2",15,"2,5","065B1514",null,"КПСР",null,"1-1-15-2,5-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFS2",15,"4","065B1515",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",20,"6,3","065B1520",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",25,"10","065B1525",null,"КПСР",null,"1-1-25-10-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",32,"16","065B1532",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",40,"25","065B1540",null,"КПСР",null,"1-1-40-25-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",50,"40","065B1550",null,"КПСР",null,"1-1-50-40-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",65,"63","065B3365",null,"КПСР",null,"1-1-65-63-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",80,"100","065B3380",null,"КПСР",null,"1-1-80-100-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFS2",100,"145","065B3400",null,"КПСР",null,"1-1-100-145-Х.ХХХХ-ВЧ-2,5-1-220-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFG2_25","index":12,"n_rows":43,"n_cols":27,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,26],[41,0,41,26],[42,0,42,26],[16,17,16,26],[1,10,1,12],[14,17,14,26],[14,3,14,12],[11,17,12,26],[11,3,12,12]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFG2",null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 200"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))",null,null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)"]
["Рабочая температура",null,null,"max +200°С",null,null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +220°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,null,null,15,20,25,32,40,50,65,80,100,125]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,null,null,null,null,4,6.3,8,16,20,32,"50",80,"125","160"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,25,32,"100","100","250"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,"40",null,"160"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"10",null,null,null,63]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,"80"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFGS2",15,"4","065B2401",null,"КПСР",null,null,"1-1-15-4-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",20,"6,3","065B2402",null,"КПСР",null,null,"1-1-20-6,3-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",25,"8","065B2403",null,"КПСР",null,null,"1-1-25-8-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",32,"16","065B2404",null,"КПСР",null,null,"1-1-32-16-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",40,"20","065B2405",null,"КПСР",null,null,"1-1-40-20-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFGS2",50,"32","065B2406",null,"КПСР",null,null,"1-1-50-32-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFGS2",65,"50","065B2407",null,"КПСР",null,null,"1-1-65-50-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",80,"80","065B2408",null,"КПСР",null,null,"1-1-80-80-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",100,"125","065B2409",null,"КПСР",null,null,"1-1-100-125-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",125,"160","065B2410",null,"КПСР",null,null,"1-1-125-160-Х.ХХХХ-ВЧ-2,5-1-220-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFG2_40","index":13,"n_rows":46,"n_cols":33,"rows_kept":46,"cut":false,"hidden":false,"merged":[[43,0,43,22],[44,0,44,22],[45,0,45,22],[1,12,1,17],[2,12,2,17],[3,14,3,19],[7,26,8,26],[7,27,8,28],[16,20,16,32],[11,3,12,15],[11,20,12,32],[14,3,14,15],[14,20,14,32]]}
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFG2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 210"]
[]
["Рабочее давление",null,null,"4 МПа (40 атм)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"4 МПа (40 атм)"]
["Материал корпуса",null,null,"Сталь 20 (GP240GH (GS-C 25))",null,null,null,null,null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Материал корпуса: Сталь 20 (1.0443)"]
["Рабочая температура",null,null,"max +200°С",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +425°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250,null,null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,400,null,null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360","400"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"25","40","63","100","160","250","450"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,32,"63",80,125,250,"450","630"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,25,"40","100","100","250","360","630","800"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,63,null,"160",null,null,null,1000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"10"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1,6"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"2,5"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFGS2",15,"4","065B2411",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",20,"6,3","065B2412",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",25,"8","065B2413",null,"КПСР",null,"1-1-25-8-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",32,"16","065B2414",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-СТ-4-1-425-У",null,null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFGS2",40,"20","065B2415",null,"КПСР",null,"1-1-40-20-Х.ХХХХ-СТ-4-1-425-У",null,null,null,null,null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFGS2",50,"32","065B2416",null,"КПСР",null,"1-1-50-32-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",65,"50","065B2417",null,"КПСР",null,"1-1-65-50-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",80,"80","065B2418",null,"КПСР",null,"1-1-80-80-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",100,"125","065B2419",null,"КПСР",null,"1-1-100-125-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",125,"160","065B2420",null,"КПСР",null,"1-1-125-160-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",150,"280","065B2421",null,"КПСР",null,"1-1-150-280-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",200,"320","065B2422",null,"КПСР",null,"1-1-200-320-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",250,"400","065B2423",null,"КПСР",null,"1-1-250-400-Х.ХХХХ-СТ-4-1-425-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFGS2_16","index":14,"n_rows":44,"n_cols":33,"rows_kept":44,"cut":false,"hidden":false,"merged":[[41,0,41,22],[42,0,42,22],[43,0,43,22],[16,20,16,32],[1,12,1,17],[2,12,2,17],[3,12,3,17],[7,26,8,26],[7,27,8,28],[11,3,12,15],[11,20,12,32],[14,3,14,15],[14,20,14,32]]}
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFGS2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 100"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-GJL-250 (GG-25))",null,null,null,null,null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +350°С",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250,null,null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,400,null,null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360","400"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100","160","250","450"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,250,"450","630"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,25,32,"100","100","250","360","630","800"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,1000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"10",null,null,null,63]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,"80"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFGS2",15,"4","065B2430",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",20,"6,3","065B2431",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",25,"8","065B2432",null,"КПСР",null,"1-1-25-8-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",32,"16","065B2433",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",40,"20","065B2434",null,"КПСР",null,"1-1-40-20-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFGS2",50,"32","065B2435",null,"КПСР",null,"1-1-50-32-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFGS2",65,"50","065B2436",null,"КПСР",null,"1-1-65-50-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",80,"80","065B2437",null,"КПСР",null,"1-1-80-80-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",100,"125","065B2438",null,"КПСР",null,"1-1-100-125-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",125,"160","065B2439",null,"КПСР",null,"1-1-125-160-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",150,"280","065B2440",null,"КПСР",null,"1-1-150-280-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",200,"320","065B2441",null,"КПСР",null,"1-1-200-320-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VFGS2",250,"400","065B2442",null,"КПСР",null,"1-1-250-400-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFGS2_25","index":15,"n_rows":43,"n_cols":27,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,22],[41,0,41,22],[42,0,42,22],[11,3,12,12],[11,17,12,26],[14,3,14,12],[14,17,14,26],[16,17,16,26],[3,13,3,16],[7,25,8,25],[7,26,8,26],[1,11,1,16],[2,11,2,16]]}
[]
[null,null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFGS2",null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 200"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))",null,null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)"]
["Рабочая температура",null,null,"max +350°С",null,null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +220°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,null,null,15,20,25,32,40,50,65,80,100,125]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,null,null,null,null,4,6.3,8,16,20,32,"50",80,"125","160"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,25,32,"100","100","250"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,"40",null,"160"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"10",null,null,null,63]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,"80"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFGS2",15,"4","065B2443",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",20,"6,3","065B2444",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",25,"8","065B2445",null,"КПСР",null,"1-1-25-8-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",32,"16","065B2446",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFGS2",40,"20","065B2447",null,"КПСР",null,"1-1-40-20-Х.ХХХХ-ВЧ-2,5-1-220-У",null,null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFGS2",50,"32","065B2448",null,"КПСР",null,"1-1-50-32-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",65,"50","065B2449",null,"КПСР",null,"1-1-65-50-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",80,"80","065B2450",null,"КПСР",null,"1-1-80-80-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",100,"125","065B2451",null,"КПСР",null,"1-1-100-125-Х.ХХХХ-ВЧ-2,5-1-220-У"]
["Danfoss","VFGS2",125,"160","065B2452",null,"КПСР",null,"1-1-125-160-Х.ХХХХ-ВЧ-2,5-1-220-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VFGS2_40","index":16,"n_rows":44,"n_cols":33,"rows_kept":44,"cut":false,"hidden":false,"merged":[[41,0,41,22],[42,0,42,22],[43,0,43,22],[11,3,12,15],[11,20,12,32],[14,3,14,15],[16,20,16,32],[14,20,14,32],[1,14,1,19],[2,14,2,19],[3,14,3,19],[7,26,8,26],[7,27,8,29]]}
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VFGS2",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 210"]
[]
["Рабочее давление",null,null,"4 МПа (40 атм)",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"4 МПа (40 атм)"]
["Материал корпуса",null,null,"Сталь 20 (GP240GH (GS-C 25))",null,null,null,null,null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Сталь 20 (1.0443)"]
["Рабочая температура",null,null,"max +350°С",null,null,null,null,null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +425°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250,null,null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,250]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,400,null,null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360","400"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100","160","250","450"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,250,"450","630"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,25,32,"100","100","250","360","630","800"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,1000]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"10",null,null,null,63]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,"80"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VFGS2",15,"4","065B2453",null,"КПСР",null,"1-1-15-4-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",20,"6,3","065B2454",null,"КПСР",null,"1-1-20-6,3-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",25,"8","065B2455",null,"КПСР",null,"1-1-25-8-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",32,"16","065B2456",null,"КПСР",null,"1-1-32-16-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",40,"20","065B2457",null,"КПСР",null,"1-1-40-20-Х.ХХХХ-СТ-4-1-425-У",null,null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VFGS2",50,"32","065B2458",null,"КПСР",null,"1-1-50-32-Х.ХХХХ-СТ-4-1-425-У",null,null,null,null,null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VFGS2",65,"50","065B2459",null,"КПСР",null,"1-1-65-50-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",80,"80","065B2460",null,"КПСР",null,"1-1-80-80-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",100,"125","065B2461",null,"КПСР",null,"1-1-100-125-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",125,"160","065B2462",null,"КПСР",null,"1-1-125-160-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",150,"280","065B2463",null,"КПСР",null,"1-1-150-280-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",200,"320","065B2464",null,"КПСР",null,"1-1-200-320-Х.ХХХХ-СТ-4-1-425-У"]
["Danfoss","VFGS2",250,"400","065B2465",null,"КПСР",null,"1-1-250-400-Х.ХХХХ-СТ-4-1-425-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VM2","index":17,"n_rows":48,"n_cols":17,"rows_kept":48,"cut":false,"hidden":false,"merged":[[45,0,45,17],[46,0,46,17],[47,0,47,17],[21,11,21,16],[1,7,1,12],[2,7,2,12],[3,8,3,13],[14,11,14,16],[14,3,14,8],[11,11,12,16],[11,3,12,8]]}
[]
[null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VМ 2",null,null,null,null,null,null,null,"Клапан КПСР серии 110"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,"Рабочее давление",null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Красная бронза (Rg 5)",null,null,null,null,null,"Материал корпуса",null,"Высокопрочный чугун (EN-JS 1025)"]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,"Рабочая температура",null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.25,4,6.3,10,16,25,null,null,0.25,4,6.3,10,16,25]
[null,null,null,0.4,6.3,8,null,null,null,null,null,0.4,6.3,8]
[null,null,null,0.63,null,null,null,null,null,null,null,0.63]
[null,null,null,1,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,1.6]
[null,null,null,2.5,null,null,null,null,null,null,null,2.5]
[null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,3.2,2.5,2.5,16,20,16]
[null,null,null,null,null,null,null,null,null,null,null,4,null,4,null,25,32]
[null,null,null,null,null,null,null,null,null,null,null,null,null,10,null,null,40]
[]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VM2",15,"0,25","065B2010",null,"КПСР",null,"1-1-15-0,25-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",15,"0,4","065B2011",null,"КПСР",null,"1-1-15-0,4-1.3500-ВЧ-2,5-1-150-У",null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VM2",15,"0,63","065B2012",null,"КПСР",null,"1-1-15-0,63-1.3500-ВЧ-2,5-1-150-У",null,null,"уточняйте у сотрудников компании"]
["Danfoss","VM2",15,"1","065B2013",null,"КПСР",null,"1-1-15-1.1-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",15,"1,6","065B2014",null,"КПСР",null,"1-1-15-1,6-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",15,"2,5","065B2015",null,"КПСР",null,"1-1-15-2,5-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",20,"4","065B2016",null,"КПСР",null,"1-1-20-4-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",20,"6,3","065B2027",null,"КПСР",null,"1-1-20-6,3-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",25,"6,3","065B2017",null,"КПСР",null,"1-1-25-6,3-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",25,"8","065B2028",null,"КПСР",null,"1-1-25-8-1.3500-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",32,"10","065B2018",null,"КПСР",null,"1-1-32-10-1.3501-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",40,"16","065B2019",null,"КПСР",null,"1-1-40-16-1.3501-ВЧ-2,5-1-150-У"]
["Danfoss","VM2",50,"25","065B2020",null,"КПСР",null,"1-1-50-25-1.3501-ВЧ-2,5-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VRB2","index":18,"n_rows":43,"n_cols":19,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,19],[41,0,41,19],[42,0,42,19],[20,13,20,18],[14,13,14,18],[14,3,14,8],[1,8,1,15],[2,8,2,15],[3,8,3,15],[11,13,12,18],[11,3,12,8]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VRB 2",null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 110"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Красная бронза (Rg 5)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +130°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.63,6.3,10,16,25,40,null,null,null,null,0.63,4,6.3,10,16,25]
[null,null,null,1,null,null,null,null,null,null,null,null,null,1,6.3,8]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,16,20,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,null,4,null,25,32]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,10,null,null,40]
[]
[]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VRB2",15,"0,63","065Z0171",null,"КПСР",null,"1-1-15-0,63-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1","065Z0172",null,"КПСР",null,"1-1-15-1.1-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1,6","065Z0173",null,"КПСР",null,"1-1-15-1,6-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"2,5","065Z0174",null,"КПСР",null,"1-1-15-2,5-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VRB2",15,"4","065Z0175",null,"КПСР",null,"1-1-15-4-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VRB2",20,"6,3","065Z0176",null,"КПСР",null,"1-1-20-6,3-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",25,"10","065Z0177",null,"КПСР",null,"1-1-25-10-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",32,"16","065Z0178",null,"КПСР",null,"1-1-32-16-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",40,"25","065Z0179",null,"КПСР",null,"1-1-40-25-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",50,"40","065Z0180",null,"КПСР",null,"1-1-50-40-1.3501-СЧ-1,6-1-150-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VRG2","index":19,"n_rows":43,"n_cols":19,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,19],[41,0,41,19],[42,0,42,19],[20,13,20,18],[14,13,14,18],[14,3,14,8],[1,8,1,15],[2,8,2,15],[3,8,3,15],[11,13,12,18],[11,3,12,8]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VRG 2",null,null,null,null,null,null,null,null,null,"Клапан КПСР серии 110"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (GG-25)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +130°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.63,6.3,10,16,25,40,null,null,null,null,0.63,6.3,10,16,25,40]
[null,null,null,1,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,4,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,1.6,2.5,10,20,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,2.5,4,null,16,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,6.3,null,null,32]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Производитель",null,null,"Маркировка"]
["Danfoss","VRB2",15,"0,63","065Z0131",null,"КПСР",null,"1-1-15-0,63-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1","065Z0132",null,"КПСР",null,"1-1-15-1-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1,6","065Z0133",null,"КПСР",null,"1-1-15-1,6-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"2,5","065Z0134",null,"КПСР",null,"1-1-15-2,5-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"4","065Z0135",null,"КПСР",null,"1-1-15-4-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VRB2",20,"6,3","065Z0136",null,"КПСР",null,"1-1-20-6,3-1.3500-СЧ-1,6-1-150-У",null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VRB2",25,"10","065Z0137",null,"КПСР",null,"1-1-25-10-1.3500-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",32,"16","065Z0138",null,"КПСР",null,"1-1-32-16-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",40,"25","065Z0139",null,"КПСР",null,"1-1-40-25-1.3501-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",50,"40","065Z0140",null,"КПСР",null,"1-1-50-40-1.3501-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VL3","index":20,"n_rows":45,"n_cols":25,"rows_kept":45,"cut":false,"hidden":false,"merged":[[42,0,42,19],[43,0,43,19],[44,0,44,19],[14,16,14,24],[14,3,14,11],[20,16,20,24],[1,10,1,15],[2,10,2,15],[3,10,3,15],[11,16,12,24],[11,3,12,11]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VL3",null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КССР серии 100"]
[]
["Рабочее давление",null,null,"0,6 МПа (6 атм)",null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +120°С",null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,null,null,null,null,15,20,25,32,40,50,65,80,100]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"0,63",6.3,10,16,25,40,63,100,145,null,null,null,null,0.63,6.3,"10",16,"25","40","63","100","160"]
[null,null,null,"1",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,"2,5",null,null,null,null,null,null,null,null,null,null,null,null,"2,5"]
[null,null,null,"4",null,null,null,null,null,null,null,null,null,null,null,null,"4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,1.6,1.6,6.3,10,16,"25","40",80]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5,2.5,10,16,25,40,"63","100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,null,null,null,null,80,"125"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.3]
[]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,null,"Маркировка"]
["Danfoss","VL3",15,"0,63","065Z0351",null,"КССР",null,"1-15-0,63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",15,"1","065Z0352",null,"КССР",null,"1-15-1-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",15,"1,6","065Z0353",null,"КССР",null,"1-15-1,6-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",15,"2,5","065Z0354",null,"КССР",null,"1-15-2,5-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",15,"4","065Z0355",null,"КССР",null,"1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VL3",20,"6,3","065Z0356",null,"КССР",null,"1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VL3",25,"10","065Z0357",null,"КССР",null,"1-25-10-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",32,"16","065Z0358",null,"КССР",null,"1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",40,"25","065Z0359",null,"КССР",null,"1-40-25-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",50,"40","065Z0360",null,"КССР",null,"1-50-40-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",65,"63","065Z0361",null,"КССР",null,"1-65-63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",80,"100","065Z0362",null,"КССР",null,"1-80-100-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VL3",100,"145","065Z3413",null,"КССР",null,"1-100-145-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VF3","index":21,"n_rows":45,"n_cols":25,"rows_kept":45,"cut":false,"hidden":false,"merged":[[42,0,42,19],[43,0,43,19],[44,0,44,19],[20,16,20,24],[1,10,1,13],[3,10,3,13],[11,16,12,24],[11,3,12,11],[14,16,14,24],[14,3,14,11]]}
[]
[null,null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfos серии VF3",null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КССР серии 100"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +130 (150) °С",null,null,null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,65,80,100,null,null,null,null,15,20,25,32,40,50,65,80,100]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,"0,63",6.3,10,16,25,40,63,100,145,null,null,null,null,0.63,6.3,"10",16,"25","40","63","100","160"]
[null,null,null,"1",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,"2,5",null,null,null,null,null,null,null,null,null,null,null,null,"2,5"]
[null,null,null,"4",null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значния"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,1.6,1.6,6.3,10,16,"25","40",80]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,2.5,2.5,10,16,25,40,"63","100"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4,4,null,null,null,"56",80,"125"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,null,"Маркировка"]
["Danfoss","VF3",15,"0,63","065Z0251",null,"КССР",null,"1-15-0,63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",15,"1","065Z0252",null,"КССР",null,"1-15-1-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",15,"1,6","065Z0253",null,"КССР",null,"1-15-1,6-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",15,"2,5","065Z0254",null,"КССР",null,"1-15-2,5-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",15,"4","065Z0255",null,"КССР",null,"1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",20,"6,3","065Z0256",null,"КССР",null,"1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VF3",25,"10","065Z0257",null,"КССР",null,"1-25-10-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VF3",32,"16","065Z0258",null,"КССР",null,"1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",40,"25","065Z0259",null,"КССР",null,"1-40-25-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",50,"40","065Z0260",null,"КССР",null,"1-50-40-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",65,"63","065Z0261",null,"КССР",null,"1-65-63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",80,"100","065Z0262",null,"КССР",null,"1-80-100-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VF3",100,"145","065Z1685",null,"КССР",null,"1-100-145-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VRB3","index":22,"n_rows":42,"n_cols":19,"rows_kept":42,"cut":false,"hidden":false,"merged":[[39,0,39,19],[40,0,40,19],[41,0,41,19],[20,13,20,18],[14,13,14,18],[14,3,14,8],[1,8,1,15],[2,8,2,15],[3,8,3,15],[11,13,12,18],[11,3,12,8]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VRB 3",null,null,null,null,null,null,null,null,null,"Клапан КССР серии 100"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Красная бронза (Rg 5)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +130°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.63,6.3,10,16,25,40,null,null,null,null,0.63,6.3,10,16,25,40]
[null,null,null,1,null,null,null,null,null,null,null,null,null,1]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,20,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,6.3,null,null,32]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,null,"Маркировка"]
["Danfoss","VRB2",15,"0,63","065Z0151",null,"КССР",null,"1-15-0,63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1","065Z0152",null,"КССР",null,"1-15-1-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1,6","065Z0153",null,"КССР",null,"1-15-1,6-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"2,5","065Z0154",null,"КССР",null,"1-15-2,5-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"4","065Z0155",null,"КССР",null,"1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VRB2",20,"6,3","065Z0156",null,"КССР",null,"1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VRB2",25,"10","065Z0157",null,"КССР",null,"1-25-10-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",32,"16","065Z0158",null,"КССР",null,"1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",40,"25","065Z0159",null,"КССР",null,"1-40-25-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",50,"40","065Z0160",null,"КССР",null,"1-50-40-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия VRG3","index":23,"n_rows":43,"n_cols":19,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,19],[41,0,41,19],[42,0,42,19],[15,13,15,18],[21,13,21,18],[14,13,14,18],[14,3,14,8],[1,8,1,15],[2,8,2,15],[3,8,3,15],[11,13,12,18],[11,3,12,8]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Клапан Danfoss серии VRG 3",null,null,null,null,null,null,null,null,null,"Клапан КССР серии100"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (GG-25)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +130°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм"]
[]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
[null,null,null,0.63,6.3,10,16,25,40,null,null,null,null,"Основные значения"]
[null,null,null,1,null,null,null,null,null,null,null,null,null,0.63,6.3,10,16,25,40]
[null,null,null,1.6,null,null,null,null,null,null,null,null,null,1]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,4,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,20,25]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,6.3,null,null,32]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,null,"Маркировка",null,null,null,null,null,8]
["Danfoss","VRB2",15,"0,63","065Z0111",null,"КССР",null,"1-15-0,63-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1","065Z0112",null,"КССР",null,"1-15-1-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"1,6","065Z0113",null,"КССР",null,"1-15-1,6-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"2,5","065Z0114",null,"КССР",null,"1-15-2,5-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",15,"4","065Z0115",null,"КССР",null,"1-15-4-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",20,"6,3","065Z0116",null,"КССР",null,"1-20-6,3-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",25,"10","065Z0117",null,"КССР",null,"1-25-10-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,"Применяемость приводов к конкретному диаметру "]
["Danfoss","VRB2",32,"16","065Z0118",null,"КССР",null,"1-32-16-Х.ХХХХ-СЧ-1,6-1-150-У",null,null,null,null,"уточняйте у сотрудников компании"]
["Danfoss","VRB2",40,"25","065Z0119",null,"КССР",null,"1-40-25-Х.ХХХХ-СЧ-1,6-1-150-У"]
["Danfoss","VRB2",50,"40","065Z0120",null,"КССР",null,"1-50-40-Х.ХХХХ-СЧ-1,6-1-150-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AVP","index":24,"n_rows":49,"n_cols":29,"rows_kept":49,"cut":false,"hidden":false,"merged":[[46,0,46,19],[47,0,47,19],[48,0,48,19],[20,13,20,18],[32,21,32,22],[29,21,29,22],[30,4,30,8],[30,10,31,13],[30,14,30,19],[30,20,31,23],[32,4,32,5],[32,8,32,9],[32,11,32,12],[32,14,32,15],[32,18,32,19],[29,11,29,12],[5,24,5,28],[16,3,16,8],[16,13,16,18],[6,22,7,22],[1,7,1,14],[2,7,2,14],[3,8,3,15],[5,22,5,23],[6,23,7,23],[13,3,14,8],[13,13,14,18]]}
[]
[null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Регулятор перепада давления Danfoss серии AVP",null,null,null,null,null,null,null,null,null,"Регулятор перепада давления РА-М серии 100",null,null,null,null,null,null,null,null,"Danfoss",null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,2-1","0,3-2",0,1,2,3,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"для внутренних сетей и ИТП",null,null,null,null,null,null,null,"атм",null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,0.1]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,0.2]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм",null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,3]
[null,null,null,1.6,6.3,8,12.5,20,25,null,null,null,null,1.6,6.3,8,16,20,25,null,null,4]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,2.5,null,null,null,null,null,null,null,6]
[null,null,null,4,null,null,null,null,null,null,null,null,null,4,null,null,null,null,null,null,null,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,null,null,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,null,null,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,32,null,null,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,null,null,"Диапазону 0,2-1 соответствует диапазон 0,1-1"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,10,null,null,null,null,null,"Диапазону 0,3-2 соответствует диапазон 0,1-1,6 или 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,null,null,null,"Заменить"]
[null,null,null,null,"Обратный трубопровод",null,null,null,null,null," значение -Х- на 0, 1 или 2 в зависимости от диапазона настройки согласно таблице ",null,null,null,"Подающий трубопровод",null,null,null,null,null," значение -Х- на 0, 1 или 2 в зависимости от диапазона настройки согласно таблице "]
[null,null,null,null,"Настройка 0,2-1,0","Настройка 0,3-2,0",null,null,null,null,null,null,null,null,"Настройка 0,2-1,0","Настройка 0,3-2,0"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,"Маркировка",null,null,"Артикул",null,"Изделие",null,"Маркировка",null,null,"Маркировка"]
["Danfoss","AVP",15,"1,6","003H06283","003H06293","РА-М",null,"15-1,6-0-СЧ-1,6-1-150-У",null,null,"15-1,6-Х-СЧ-1,6-1-150-У",null,null,"003H6325","003H6315","РА-М",null,"15-1,6-0-СЧ-1,6-1-150-У",null,null,"15-1,6-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",15,"2,5","003H06284","003H06294","РА-М",null,"15-2,5-0-СЧ-1,6-1-150-У",null,null,"15-2,5-Х-СЧ-1,6-1-150-У",null,null,"003H6326","003H6316","РА-М",null,"15-2,5-0-СЧ-1,6-1-150-У",null,null,"15-2,5-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",15,"4","003H06285","003H06295","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У",null,null,"003H6327","003H6317","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",20,"6,3","003H06286","003H06296","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У",null,null,"003H6328","003H6318","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",25,"8","003H06287","003H06297","РА-М",null,"25-8-0-СЧ-1,6-1-150-У",null,null,"25-8-Х-СЧ-1,6-1-150-У",null,null,"003H6329","003H6319","РА-М",null,"25-8-0-СЧ-1,6-1-150-У",null,null,"25-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",15,"4","003H06345","003H06351","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У",null,null,"003H6375","003H6369","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",20,"6,3","003H06346","003H06352","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У",null,null,"003H6376","003H6370","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",25,"8","003H06347","003H06353","РА-М",null,"20-8-0-СЧ-1,6-1-150-У",null,null,"20-8-Х-СЧ-1,6-1-150-У",null,null,"003H6377","003H6371","РА-М",null,"20-8-0-СЧ-1,6-1-150-У",null,null,"20-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",32,"12,5","003H06348","003H06354","РА-М",null,"32-16-0-СЧ-1,6-1-150-У",null,null,"32-16-Х-СЧ-1,6-1-150-У",null,null,"003H6378","003H6372","РА-М",null,"32-16-0-СЧ-1,6-1-150-У",null,null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",40,"20","003H06349","003H06355","РА-М",null,"40-20-0-СЧ-1,6-1-150-У",null,null,"40-20-Х-СЧ-1,6-1-150-У",null,null,"003H6379","003H6373","РА-М",null,"40-20-0-СЧ-1,6-1-150-У",null,null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVP",50,"25","003H06350","003H06356","РА-М",null,"50-25-0-СЧ-1,6-1-150-У",null,null,"50-25-Х-СЧ-1,6-1-150-У",null,null,"003H6380","003H6374","РА-М",null,"50-25-0-СЧ-1,6-1-150-У",null,null,"50-25-Х-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия DPR","index":25,"n_rows":49,"n_cols":29,"rows_kept":49,"cut":false,"hidden":false,"merged":[[46,0,46,19],[47,0,47,19],[48,0,48,19],[30,20,31,23],[29,21,29,22],[32,4,32,5],[30,4,30,8],[29,11,29,12],[30,10,31,13],[30,14,30,19],[32,8,32,9],[32,11,32,12],[32,18,32,19],[32,21,32,22],[32,14,32,15],[16,3,16,8],[16,13,16,18],[13,3,14,8],[13,13,14,18],[20,13,20,18],[5,22,5,23],[5,24,5,28],[6,22,7,22],[6,23,7,23],[1,7,1,14],[2,7,2,14],[3,8,3,15]]}
[]
[null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Регулятор перепада давления Danfoss серии DPR",null,null,null,null,null,null,null,null,null,"Регулятор перепада давления РА-М серии 100",null,null,null,null,null,null,null,null,"Danfoss",null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,2-1","0,3-2",0,1,2,3,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"для внутренних сетей и ИТП",null,null,null,null,null,null,null,"атм",null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,0.1]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,0.2]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм",null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,3]
[null,null,null,1.6,6.3,8,12.5,20,25,null,null,null,null,1.6,6.3,8,16,20,25,null,null,4]
[null,null,null,2.5,null,null,null,null,null,null,null,null,null,2.5,null,null,null,null,null,null,null,6]
[null,null,null,4,null,null,null,null,null,null,null,null,null,4,null,null,null,null,null,null,null,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,null,null,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,null,null,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,32,null,null,16]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,null,null,"Диапазону 0,2-1 соответствует диапазон 0,1-1"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,10,null,null,null,null,null,"Диапазону 0,3-2 соответствует диапазон 0,1-1,6 или 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,3.2,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,null,null,null,"Заменить"]
[null,null,null,null,"Обратный трубопровод",null,null,null,null,null," значение -Х- на 0, 1 или 2 в зависимости от диапазона настройки согласно таблице ",null,null,null,"Подающий трубопровод",null,null,null,null,null," значение -Х- на 0, 1 или 2 в зависимости от диапазона настройки согласно таблице "]
[null,null,null,null,"Настройка 0,2-1,0","Настройка 0,3-2,0",null,null,null,null,null,null,null,null,"Настройка 0,2-1,0","Настройка 0,3-2,0"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,"Маркировка",null,null,"Артикул",null,"Изделие",null,"Маркировка",null,null,"Маркировка"]
["Danfoss","DPR",15,"1,6","003H6122","003H6133","РА-М",null,"15-1,6-0-СЧ-1,6-1-150-У",null,null,"15-1,6-Х-СЧ-1,6-1-150-У",null,null,"003H6111","003H6100","РА-М",null,"15-1,6-0-СЧ-1,6-1-150-У",null,null,"15-1,6-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",15,"2,5","003H6123","003H6134","РА-М",null,"15-2,5-0-СЧ-1,6-1-150-У",null,null,"15-2,5-Х-СЧ-1,6-1-150-У",null,null,"003H6112","003H6101","РА-М",null,"15-2,5-0-СЧ-1,6-1-150-У",null,null,"15-2,5-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",15,"4","003H6124","003H6135","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У",null,null,"003H6113","003H6102","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",20,6.3,"003H6125","003H6136","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У",null,null,"003H6114","003H6103","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",25,"8","003H6126","003H6137","РА-М",null,"25-8-0-СЧ-1,6-1-150-У",null,null,"25-8-Х-СЧ-1,6-1-150-У",null,null,"003H6115","003H6104","РА-М",null,"25-8-0-СЧ-1,6-1-150-У",null,null,"25-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",15,"4","003H6127","003H6138","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У",null,null,"003H6116","003H6105","РА-М",null,"15-4-0-СЧ-1,6-1-150-У",null,null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",20,"6,3","003H6128","003H6139","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У",null,null,"003H6117","003H6106","РА-М",null,"20-6,3-0-СЧ-1,6-1-150-У",null,null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",25,"8","003H6129","003H6140","РА-М",null,"20-8-0-СЧ-1,6-1-150-У",null,null,"20-8-Х-СЧ-1,6-1-150-У",null,null,"003H6118","003H6107","РА-М",null,"20-8-0-СЧ-1,6-1-150-У",null,null,"20-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",32,"12,5","003H6130","003H6141","РА-М",null,"32-16-0-СЧ-1,6-1-150-У",null,null,"32-16-Х-СЧ-1,6-1-150-У",null,null,"003H6119","003H6108","РА-М",null,"32-16-0-СЧ-1,6-1-150-У",null,null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",40,20,"003H6131","003H6142","РА-М",null,"40-20-0-СЧ-1,6-1-150-У",null,null,"40-20-Х-СЧ-1,6-1-150-У",null,null,"003H6120","003H6109","РА-М",null,"40-20-0-СЧ-1,6-1-150-У",null,null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","DPR",50,25,"003H6132","003H6143","РА-М",null,"50-25-0-СЧ-1,6-1-150-У",null,null,"50-25-Х-СЧ-1,6-1-150-У",null,null,"003H6121","003H6110","РА-М",null,"50-25-0-СЧ-1,6-1-150-У",null,null,"50-25-Х-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AVA","index":26,"n_rows":43,"n_cols":30,"rows_kept":43,"cut":false,"hidden":false,"merged":[[40,0,40,19],[41,0,41,19],[42,0,42,19],[30,4,30,5],[30,9,30,10],[27,8,29,11],[28,4,29,4],[28,5,29,5],[1,7,1,14],[2,7,2,14],[3,9,3,16],[13,3,14,9],[13,14,14,19],[26,9,26,10],[5,23,5,24],[5,25,5,29],[5,22,7,22],[6,23,7,23],[6,24,7,24],[19,14,19,19],[16,3,16,9],[16,14,16,19]]}
[]
[null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Регулятор давления \"до себя\" Danfoss серии AVA",null,null,null,null,null,null,null,null,null,null,"Регулятор давления \"до себя\" РА-В серии 100",null,null,null,null,null,null,null,"атм","Danfoss",null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"для внутренних сетей и ИТП",null,null,null,null,null,null,null,null,"1-4,5","3-11",0,1,2,3,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,0.1]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT)",null,null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,0.2]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,"Dn, мм",null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,null,40,50,null,null,null,null,15,20,25,32,40,50,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,12.5,null,20,25,null,null,null,null,4,6.3,8,16,20,25,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,null,null,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,null,null,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,32,null,null,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,null,null,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,10,null,null,null,null,null,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,null,null,12]
[null,null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,3.2,null,null,null,null,null,null,null,16]
[null,null,null,null,null,null,null,null," значение -Х- на 2, 3 или 4 в зависимости от диапазона настройки согласно таблице "]
[null,null,null,null,"Настройка   1 - 4,5","Настройка   3 - 11",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-4,5 соответствует диапазон 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 3-11 соответствует диапазон 3-7 или 6-12"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,null,"Изделие",null,"Маркировка",null,null,null,null,null,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Danfoss","AVA",15,"4","003H06614","003H6620",null,"РА-В",null,"15-4-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AVA",20,"6,3","003H06615","003H6621",null,"РА-В",null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVA",25,"8","003H06616","003H6622",null,"РА-В",null,"20-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVA",32,"12,5","003H06626","003H6629",null,"РА-В",null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVA",40,20,"003H06627","003H6630",null,"РА-В",null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVA",50,25,"003H06628","003H6631",null,"РА-В",null,"50-25-Х-СЧ-1,6-1-150-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AVD","index":27,"n_rows":42,"n_cols":29,"rows_kept":42,"cut":false,"hidden":false,"merged":[[39,0,39,19],[40,0,40,19],[41,0,41,19],[30,4,30,5],[30,8,30,9],[28,4,29,4],[28,5,29,5],[27,7,29,10],[13,3,14,8],[13,13,14,18],[16,3,16,8],[16,13,16,18],[26,8,26,9],[17,13,17,18],[19,13,19,18],[5,22,5,23],[5,24,5,28],[6,22,7,22],[6,23,7,23],[1,8,1,15],[2,8,2,15],[3,8,3,15],[5,21,7,21]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,"Регулятор давления \"после себя\" Danfoss серии AVD",null,null,null,null,null,null,null,null,null,"Регулятор давления \"после себя\" РА-А серии 100",null,null,null,null,null,null,null,"атм","Danfoss",null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"для внутренних сетей и ИТП",null,null,null,null,null,null,null,null,"1-5","3-12",0,1,2,3,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,"Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,"2,5 МПа (25 атм)",null,null,null,0.1]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT)",null,null,null,null,null,null,"Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,"Высокопрочный чугун (EN-JS 1025)",null,null,null,0.2]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,"Рабочая температура",null,null,"max +150°С",null,null,null,"max +150°С",null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,"Dn, мм",null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,40,50,null,null,null,null,15,20,25,32,40,50,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,12.5,20,25,null,null,null,null,"Основные значения",null,null,null,null,null,null,null,4]
[null,null,null,null,null,null,null,null,null,null,null,null,null,4,6.3,8,16,20,25,null,null,5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,6]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,6.3,10,10,null,null,7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,10,16,16,null,null,8]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.4,4,4,null,25,32,null,null,10]
[null,null,null,null,null,null,null,null,null,null,null,null,null,0.63,null,6.3,null,null,40,null,null,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,10,null,null,null,null,null,12]
[null,null,null,null,null,null,null,null,null,null,null,null,null,1.6,null,null,null,null,null,null,null,16]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,3.2,null,null,null,null,null,null,null,"Диапазону 1-4,5 соответствует диапазон 1-4 "]
[null,null,null,null,null,null,null," значение -Х- на 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 3-12 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,"Настройка  1 - 5","Настройка   3 - 12",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка"]
["Danfoss","AVD",15,"4","003H06644","003H6650","РА-А",null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVD",20,"6,3","003H06645","003H6651","РА-А",null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVD",25,"8","003H06646","003H6652","РА-А",null,"20-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVD",32,"12,5","003H06659","003H6662","РА-А",null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVD",40,20,"003H06660","003H6663","РА-А",null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","AVD",50,25,"003H06661","003H6664","РА-А",null,"50-25-Х-СЧ-1,6-1-150-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AVDS","index":28,"n_rows":41,"n_cols":23,"rows_kept":41,"cut":false,"hidden":false,"merged":[[38,0,38,19],[39,0,39,19],[40,0,40,19],[31,4,31,5],[31,8,31,9],[29,4,30,4],[29,5,30,5],[28,7,30,10],[16,3,16,5],[16,10,16,12],[6,16,6,17],[27,8,27,9],[20,10,20,12],[13,3,14,5],[13,10,14,12],[6,18,6,22],[7,16,8,16],[7,17,8,17],[6,15,8,15],[1,8,1,11],[2,8,2,11],[3,6,3,12]]}
[]
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,"Регулятор давления \"после себя\" Danfoss серии AVDS",null,null,null,null,null,null,null,"Регулятор давления \"после себя\" РА-А серии 200"]
[null,null,null,null,null,null,null,null,null,null,"для внутренних сетей и ИТП",null,null,null,null,"атм","Danfoss",null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1-5","3-12",0,1,2,3,4]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,"Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT)",null,null,null,"Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)",null,null,null,null,0.1]
["Рабочая температура",null,null,"max +150°С",null,null,null,"Рабочая температура",null,null,"max +220°С",null,null,null,null,0.2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
[null,null,null,"Dn, мм",null,null,null,null,null,null,"Dn, мм",null,null,null,null,0.7]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,15,20,25,null,null,null,null,15,20,25,null,null,1.6]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,2]
[null,null,null,1,4.5,6.3,null,null,null,null,1,4,6.3,null,null,3]
[null,null,null,1.6,null,null,null,null,null,null,1.6,null,null,null,null,4]
[null,null,null,3.2,null,null,null,null,null,null,3.2,null,null,null,null,4.5]
[null,null,null,null,null,null,null,null,null,null,"Дополнительные значения",null,null,null,null,5]
[null,null,null,null,null,null,null,null,null,null,0.16,1.6,1.6,null,null,6]
[null,null,null,null,null,null,null,null,null,null,0.25,2.5,2.5,null,null,7]
[null,null,null,null,null,null,null,null,null,null,0.4,6.3,4,null,null,8]
[null,null,null,null,null,null,null,null,null,null,0.63,null,8,null,null,10]
[null,null,null,null,null,null,null,null,null,null,4,null,10,null,null,11]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,12]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,16]
[null,null,null,null,null,null,null," значение -Х- на 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,"Диапазону 1-5 соответствует диапазон 1-4 или 3-7"]
[null,null,null,null,"Настройка  1 - 5","Настройка   3 - 12",null,null,null,null,null,null,null,null,null,"Диапазону 3-12 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AVDS",15,"1","003H06665","003H6670","РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AVDS",15,"1,6","003H06666","003H6671","РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AVDS",15,"3,2","003H06667","003H6672","РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AVDS",20,"4,5","003H06668","003H6673","РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AVDS",25,"6,3","003H06669","003H6674","РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFP-VFG2_16","index":29,"n_rows":58,"n_cols":27,"rows_kept":58,"cut":false,"hidden":false,"merged":[[55,0,55,19],[56,0,56,19],[57,0,57,19],[41,8,41,9],[37,7,39,10],[12,20,18,20],[19,19,27,19],[9,17,11,17],[9,18,9,21],[17,21,23,21],[36,8,36,9],[13,18,20,18],[12,3,12,14],[23,3,23,14],[25,3,25,14],[5,25,6,25],[5,26,6,27],[9,3,10,14],[20,3,21,14],[0,8,0,12],[9,22,9,26],[10,18,11,18],[10,21,11,21],[10,19,11,19],[10,20,11,20]]}
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор перепада давления Danfoss серии AFP/VFG2"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,15-1,5","1-6","0,1-0,7","0,5-3",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,0.1,null,null,"AFP"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,null,null,0.15,"AFP"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2]
[null,null,null,"Регулятор перепада давления РА-М серии 100",null,null,null,null,null,null,null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,null,null,0.5,null,null,null,"AFP-9"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,null,null,null,null,0.7]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,null,null,null,null,null,null,1,null,"AFP-9"]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,null,1.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360",null,null,4]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,null,null,null,4.5]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100","160","250",null,null,5]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,250,"450",null,null,6]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250","360","630",null,null,7]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,null,null,8]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,null,null,null,10]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,null,null,null,11]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,null,null,null,12]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,15-1,5 соответствует диапазон 0,4-1,6"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-6 соответствует диапазон 1-4 или 3-7"]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,null,null,"Диапазону 0,1-0,7 соответствует диапазон 0,1-1"]
[null,null,null,null,null,null,null," значение -Х- на 0, 1, 2 или 3 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,null,null,"Диапазону 0,5-3 соответствует диапазон 1-4"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка"]
["Danfoss","AFP/VFG2",15,"4","065B2388",null,"РА-М",null,"15-4-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",20,"6,3","065B2389",null,"РА-М",null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",25,"8","065B2390",null,"РА-М",null,"25-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",32,"16","065B2391",null,"РА-М",null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",40,"20","065B2392",null,"РА-М",null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",50,"32","065B2393",null,"РА-М",null,"50-32-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",65,50,"065B2394",null,"РА-М",null,"65-50-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",80,80,"065B2395",null,"РА-М",null,"80-80-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",100,125,"065B2396",null,"РА-М",null,"100-125-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",125,160,"065B2397",null,"РА-М",null,"125-160-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",150,280,"065B2398",null,"РА-М",null,"150-280-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",200,320,"065B2399",null,"РА-М",null,"200-320-Х-СЧ-1,6-1-150-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFP-VFG2_25","index":30,"n_rows":57,"n_cols":25,"rows_kept":57,"cut":false,"hidden":false,"merged":[[54,0,54,19],[55,0,55,19],[56,0,56,19],[9,20,9,24],[10,16,11,16],[10,17,11,17],[10,18,11,18],[36,8,36,9],[37,7,39,10],[41,8,41,9],[10,19,11,19],[12,3,12,12],[12,18,18,18],[13,16,20,16],[17,19,23,19],[19,17,27,17],[20,3,21,12],[23,3,23,12],[25,3,25,12],[9,3,10,12],[9,15,11,15],[9,16,9,19]]}
[null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор перепада давления Danfoss серии AFP/VFG2"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"0,15-1,5","1-6","0,1-0,7","0,5-3",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,0.1,null,null,"AFP"]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,null,null,0.15,"AFP"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2]
[null,null,null,"Регулятор перепада давления РА-М серии 200",null,null,null,null,null,null,null,null,null,null,null,0.3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,null,0.5,null,null,null,"AFP-9"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)",null,null,null,null,null,null,null,null,null,null,null,0.7]
["Рабочая температура",null,null,"max +220°С",null,null,null,null,null,null,null,null,null,null,null,1,null,"AFP-9"]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,1.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,2]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",null,null,4]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,null,4.5]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100",null,null,5]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,null,null,6]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250",null,null,7]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,8]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,null,10]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,null,11]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,null,12]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,15-1,5 соответствует диапазон 0,4-1,6"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-6 соответствует диапазон 1-4 или 3-7"]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,"Диапазону 0,1-0,7 соответствует диапазон 0,1-1"]
[null,null,null,null,null,null,null," значение -Х- на 0, 1, 2 или 3 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,"Диапазону 0,5-3 соответствует диапазон 1-4"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка"]
["Danfoss","AFP/VFG2",15,"4","065B2401",null,"РА-М",null,"15-4-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",20,"6,3","065B2402",null,"РА-М",null,"20-6,3-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",25,"8","065B2403",null,"РА-М",null,"25-8-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",32,"16","065B2404",null,"РА-М",null,"32-16-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",40,"20","065B2405",null,"РА-М",null,"40-20-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",50,"32","065B2406",null,"РА-М",null,"50-32-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",65,50,"065B2407",null,"РА-М",null,"65-50-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",80,80,"065B2408",null,"РА-М",null,"80-80-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",100,125,"065B2409",null,"РА-М",null,"100-125-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",125,160,"065B2410",null,"РА-М",null,"125-160-Х-ВЧ-2,5-1-220-У"]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFA-VFG2_16","index":31,"n_rows":54,"n_cols":29,"rows_kept":54,"cut":false,"hidden":false,"merged":[[51,0,51,19],[52,0,52,19],[53,0,53,19],[9,24,9,28],[10,17,11,17],[10,18,11,18],[10,23,11,23],[10,19,11,19],[10,20,11,20],[9,16,11,16],[9,17,9,23],[10,21,11,21],[10,22,11,22],[33,8,33,9],[37,8,37,9],[34,7,36,10],[9,3,10,14],[12,3,12,14],[20,3,21,14],[23,3,23,14],[25,3,25,14]]}
[null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор давления \"до себя\" Danfoss серии AFA/VFG2"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3-11","10-16","1-5","0,5-2,5","0,15-1,2","0,1-0,6","0,05-0,35",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,0.05]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,null,0.1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15]
[null,null,null,"Регулятор давления \"до себя\" РА-В серии 100",null,null,null,null,null,null,null,null,null,null,null,null,0.35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,null,0.5]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,null,null,null,0.6]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,1.6]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360",null,3]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100","160","250",null,5]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,250,"450",null,6]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250","360","630",null,7]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,null,10]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,null,null,11]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,null,null,12]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,null,null,16]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,null,"Диапазону 3-11 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,null,null,null," значение -Х- на 1, 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,null,"Диапазону 10-16 соответствует диапазон 6-12"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-5 соответствует диапазон 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,5-2,5 соответствует диапазон 1-4"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,null,null,null,null,null,"Диапазону 0,15-1,2 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",15,"4","065B2388",null,"РА-В",null,"15-4-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Диапазону 0,1-0,6 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",20,"6,3","065B2389",null,"РА-В",null,"20-6,3-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Диапазону 0,05-0,35 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",25,"8","065B2390",null,"РА-В",null,"25-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",32,"16","065B2391",null,"РА-В",null,"32-16-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",40,"20","065B2392",null,"РА-В",null,"40-20-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Danfoss","AFP/VFG2",50,"32","065B2393",null,"РА-В",null,"50-32-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",65,50,"065B2394",null,"РА-В",null,"65-50-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AFP/VFG2",80,80,"065B2395",null,"РА-В",null,"80-80-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",100,125,"065B2396",null,"РА-В",null,"100-125-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",125,160,"065B2397",null,"РА-В",null,"125-160-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",150,280,"065B2398",null,"РА-В",null,"150-280-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",200,320,"065B2399",null,"РА-В",null,"20-320-Х-СЧ-1,6-1-150-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFA-VFG2_25","index":32,"n_rows":54,"n_cols":27,"rows_kept":54,"cut":false,"hidden":false,"merged":[[51,0,51,19],[52,0,52,19],[53,0,53,19],[9,22,9,26],[9,3,10,12],[10,15,11,15],[10,16,11,16],[10,17,11,17],[10,18,11,18],[10,19,11,19],[10,20,11,20],[34,7,36,10],[37,8,37,9],[10,21,11,21],[12,3,12,12],[20,3,21,12],[23,3,23,12],[25,3,25,12],[33,8,33,9],[9,14,11,14],[9,15,9,21]]}
[null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор давления \"до себя\" Danfoss серии AFA/VFG2"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"3-11","10-16","1-5","0,5-2,5","0,15-1,2","0,1-0,6","0,05-0,35",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,0.05]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,null,0.1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15]
[null,null,null,"Регулятор давления \"до себя\" РА-В серии 200",null,null,null,null,null,null,null,null,null,null,0.35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,0.5]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)",null,null,null,null,null,null,null,null,null,null,0.6]
["Рабочая температура",null,null,"max +220°С",null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,1.6]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,2.5]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",null,3]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,4]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100",null,5]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,null,6]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250",null,7]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,10]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,11]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,12]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,16]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,"Диапазону 3-11 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,null,null,null," значение -Х- на 1, 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,"Диапазону 10-16 соответствует диапазон 6-12"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-5 соответствует диапазон 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,5-2,5 соответствует диапазон 1-4"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,null,null,null,"Диапазону 0,15-1,2 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",15,"4","065B2401",null,"РА-В",null,"15-4-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Диапазону 0,1-0,6 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",20,"6,3","065B2402",null,"РА-В",null,"20-6,3-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Диапазону 0,05-0,35 соответствует диапазон 0,1-1"]
["Danfoss","AFP/VFG2",25,"8","065B2403",null,"РА-В",null,"25-8-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",32,"16","065B2404",null,"РА-В",null,"32-16-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",40,"20","065B2405",null,"РА-В",null,"40-20-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Danfoss","AFP/VFG2",50,"32","065B2406",null,"РА-В",null,"50-32-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",65,50,"065B2407",null,"РА-В",null,"65-50-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AFP/VFG2",80,80,"065B2408",null,"РА-В",null,"80-80-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",100,125,"065B2409",null,"РА-В",null,"100-125-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",125,160,"065B2410",null,"РА-В",null,"125-160-Х-ВЧ-2,5-1-220-У"]
[]
[]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFD-VFG2_16","index":33,"n_rows":55,"n_cols":28,"rows_kept":55,"cut":false,"hidden":false,"merged":[[52,0,52,19],[53,0,53,19],[54,0,54,19],[38,8,38,9],[34,7,37,10],[33,8,33,9],[9,16,11,16],[9,17,9,22],[10,21,11,21],[10,22,11,22],[9,3,10,14],[12,3,12,14],[20,3,21,14],[23,3,23,14],[25,3,25,14],[45,19,45,20],[9,23,9,27],[10,17,11,17],[10,18,11,18],[10,20,11,20],[10,19,11,19]]}
[null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор давления \"после себя\" Danfoss серии AFD/VFG2"]
[]
["Рабочее давление",null,null,"1,6 МПа (16 атм)"]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10-16","3-12","0,5-3","1-6","0,1-0,7","0,15-1,5",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,0.05]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,280,320,null,0.1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15]
[null,null,null,"Регулятор давления \"после себя\" РА-А серии 100",null,null,null,null,null,null,null,null,null,null,null,null,0.35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,null,0.5]
["Материал корпуса",null,null,"Серый чугун (EN-JS 1040)",null,null,null,null,null,null,null,null,null,null,null,null,0.6]
["Рабочая температура",null,null,"max +150°С",null,null,null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5]
[null,null,null,15,20,25,32,40,50,65,80,100,125,150,200,null,1.6]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",280,"360",null,4]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,null,null,5]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100","160","250",null,6]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,250,"450",null,7]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250","360","630",null,8]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,null,null,10]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,null,null,11]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,null,null,12]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,null,null,16]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,null,null,"Диапазону 10-16 соответствует диапазон 6-12"]
[null,null,null,null,null,null,null," значение -Х- на 0, 1, 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,null,null,"Диапазону 3-12 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,5-3 соответствует диапазон 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-6 соответствует диапазон 1-4 или 3-7"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,1-0,7 соответствует диапазон 0,1-1"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,null,null,null,null,null,"Диапазону 0,15-1,5 соответствует диапазон 0,4-1,6"]
["Danfoss","AFP/VFG2",15,"4","065B2388",null,"РА-А",null,"15-4-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Danfoss","AFP/VFG2",20,"6,3","065B2389",null,"РА-А",null,"20-6,3-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",25,"8","065B2390",null,"РА-А",null,"25-8-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",32,"16","065B2391",null,"РА-А",null,"32-16-Х-СЧ-1,6-1-150-У",null,null,null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AFP/VFG2",40,"20","065B2392",null,"РА-А",null,"40-20-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",50,"32","065B2393",null,"РА-А",null,"50-32-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",65,50,"065B2394",null,"РА-А",null,"65-50-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",80,80,"065B2395",null,"РА-А",null,"80-80-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",100,125,"065B2396",null,"РА-А",null,"100-125-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",125,160,"065B2397",null,"РА-А",null,"125-160-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",150,280,"065B2398",null,"РА-А",null,"150-280-Х-СЧ-1,6-1-150-У"]
["Danfoss","AFP/VFG2",200,320,"065B2399",null,"РА-А",null,"20-320-Х-СЧ-1,6-1-150-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Серия AFD-VFG2_25","index":34,"n_rows":53,"n_cols":26,"rows_kept":53,"cut":false,"hidden":false,"merged":[[50,0,50,19],[51,0,51,19],[52,0,52,19],[9,3,10,12],[9,14,11,14],[9,15,9,20],[9,21,9,25],[10,15,11,15],[10,16,11,16],[10,17,11,17],[10,18,11,18],[10,19,11,19],[10,20,11,20],[38,8,38,9],[45,17,45,18],[12,3,12,12],[20,3,21,12],[23,3,23,12],[25,3,25,12],[33,8,33,9],[34,7,37,10]]}
[null,null,null,null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[null,null,null,"Регулятор давления \"после себя\" Danfoss серии AFD/VFG2"]
[]
["Рабочее давление",null,null,"2,5 МПа (25 атм)"]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-GJS-400-18-LT (GGG 40.3))"]
["Рабочая температура",null,null,"max +200°С"]
[]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,"атм","Danfoss",null,null,null,null,null,"КПСР-Групп"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10-16","3-12","0,5-3","1-6","0,1-0,7","0,15-1,5",0,1,2,3,4]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,null,null,null,null,null,null,null,"0,1-1","0,4-1,6","1-4","3-7","6-12"]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,0.05]
[null,null,null,"4","6,3","8","16","20","32",50,80,125,160,null,0.1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15]
[null,null,null,"Регулятор давления \"после себя\" РА-А серии 200",null,null,null,null,null,null,null,null,null,null,0.35]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4]
["Рабочее давление",null,null,"2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,0.5]
["Материал корпуса",null,null,"Высокопрочный чугун (EN-JS 1025)",null,null,null,null,null,null,null,null,null,null,0.6]
["Рабочая температура",null,null,"max +220°С",null,null,null,null,null,null,null,null,null,null,0.7]
[null,null,null,"Dn, мм",null,null,null,null,null,null,null,null,null,null,1]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5]
[null,null,null,15,20,25,32,40,50,65,80,100,125,null,1.6]
[null,null,null,"Условная пропускная способность, м³/ч",null,null,null,null,null,null,null,null,null,null,3]
[null,null,null,4,6.3,8,16,20,32,"50",80,"125","160",null,4]
[null,null,null,"Дополнительные значения",null,null,null,null,null,null,null,null,null,null,5]
[null,null,null,0.16,1.6,1.6,6.3,10,10,"16","40","63","100",null,6]
[null,null,null,0.25,2.5,2.5,10,16,16,"25","63",80,125,null,7]
[null,null,null,0.4,4,4,null,25,25,32,"100","100","250",null,8]
[null,null,null,0.63,null,6.3,null,null,40,"40",null,"160",null,null,10]
[null,null,null,1,null,"10",null,null,null,null,null,null,null,null,11]
[null,null,null,1.6,null,null,null,null,null,63,null,null,null,null,12]
[null,null,null,3.2,null,null,null,null,null,"80",null,null,null,null,16]
[null,null,null,null,null,null,null,null,"Заменить",null,null,null,null,null,"Диапазону 10-16 соответствует диапазон 6-12"]
[null,null,null,null,null,null,null," значение -Х- на 0, 1, 2, 3 или 4 в зависимости от диапазона настройки согласно таблице ",null,null,null,null,null,null,"Диапазону 3-12 соответствует диапазон 3-7 или 6-12"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,5-3 соответствует диапазон 1-4"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 1-6 соответствует диапазон 1-4 или 3-7"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диапазону 0,1-0,7 соответствует диапазон 0,1-1"]
["Производитель","Изделие","DN","Kvs, м³/ч","Артикул",null,"Изделие",null,"Маркировка",null,null,null,null,null,"Диапазону 0,15-1,5 соответствует диапазон 0,4-1,6"]
["Danfoss","AFP/VFG2",15,"4","065B2401",null,"РА-А",null,"15-4-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Значение настраемого давления должно находится в среднем значении диапазона"]
["Danfoss","AFP/VFG2",20,"6,3","065B2402",null,"РА-А",null,"20-6,3-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",25,"8","065B2403",null,"РА-А",null,"25-8-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",32,"16","065B2404",null,"РА-А",null,"32-16-Х-ВЧ-2,5-1-220-У",null,null,null,null,null,"Также можно заказать регулятор с другими диапазона из таблицы"]
["Danfoss","AFP/VFG2",40,"20","065B2405",null,"РА-А",null,"40-20-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",50,"32","065B2406",null,"РА-А",null,"50-32-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",65,50,"065B2407",null,"РА-А",null,"65-50-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",80,80,"065B2408",null,"РА-А",null,"80-80-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",100,125,"065B2409",null,"РА-А",null,"100-125-Х-ВЧ-2,5-1-220-У"]
["Danfoss","AFP/VFG2",125,160,"065B2410",null,"РА-А",null,"125-160-Х-ВЧ-2,5-1-220-У"]
[]
["По вопросам продаж и поддержки обращайтесь:"]
[]
["Сайт: http://kpsr.nt-rt.ru  ||  Эл. почта: krp@nt-rt.ru"]

{"sheet":"Привода","index":35,"n_rows":37,"n_cols":25,"rows_kept":37,"cut":false,"hidden":false,"merged":[[24,0,24,1],[13,0,13,1],[12,0,12,1],[14,0,15,0],[16,0,18,0],[12,2,12,9],[12,10,12,12],[12,13,12,24],[22,0,22,1],[23,0,23,1],[13,13,13,15],[13,16,13,19],[13,20,13,21],[13,22,13,23],[19,6,19,7],[19,2,19,5],[19,8,19,9],[20,2,20,5],[20,6,20,7],[20,8,20,9],[19,11,19,12],[36,0,36,1],[25,0,25,1],[26,0,26,1],[27,0,27,1],[28,0,28,1],[29,0,29,1],[30,0,30,1],[31,0,31,1],[32,0,32,1],[33,0,33,1],[34,0,34,1],[35,0,35,1],[19,20,19,21],[20,20,20,21],[19,22,19,23],[20,22,20,23],[20,11,20,12],[19,13,19,15],[20,13,20,15],[19,16,19,19],[20,16,20,17],[20,18,20,19]]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Производитель",null,"AUMA",null,null,null,null,null,null,null,"SAUTER",null,null,"REGADA"]
["Тип привода",null,"ES 05-11","ES 05-11/E","ES 05-12","ES 05-12/E","ES 06-4","ES06-4/E","ES 08","ES 08/E","AVM 322","AVM 234","AVF 234","ST mini",null,null,"ST 0",null,null,null,"ST 0,1",null,"ST 1",null,"ST 2"]
["Тип управления","трехточечный","+",null,"+",null,"+",null,"+",null,"+","+","+","+","+","+","+","+","+","+","+","+","+","+","+"]
[null,"аналоговый",null,"+",null,"+",null,"+",null,"+","+","+","+"]
["Обратная связь","0-100 Ом",null,null,null,null,null,null,null,null,null,null,null,null,"+",null,null,null,"+",null,"+",null,"+",null,"+"]
[null,"0-10 В",null,"+",null,"+",null,"+",null,"+"]
[null,"4-20 мА",null,null,null,null,null,null,null,"+","+","+","+",null,null,"+",null,null,null,"+",null,"+",null,"+"]
[null,"Скорость, мм/мин","8 / 10",null,null,null,"8 / 10 / 13,2",null,"15/40",null,"10","10/15/30",null,"15",null,null,"16",null,null,null,"16",null,"32",null,"40"]
[null,"Ход штока","30",null,null,null,"40",null,"40/75",null,"20","50",null,"25",null,null,"40",null,"28",null,"50",null,"80",null,"80"]
["DN, мм","Код привода","1.3500","1.3502","1.3501","1.3503","1.3600","1.3601","1.3700","1.3701","1.2300","1.2100","1.2200","1.1100","1.1114","1.1109","1.1200","1.1204","1.1212","1.1213","1.1300","1.1309","1.1400","1.1409","1.1500"]
[15,null,"●","●","●","●","●","●","●","●","●","●","●","●","●","●"]
[20,null,"●","●","●","●","●","●","●","●","●","●","●","●","●","●"]
[25,null,"●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●"]
[32,null,"●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●","●"]
[40,null,"●","●","●","●","●","●","●","●",null,"●","●","●","●","●","●","●","●","●","●","●"]
[50,null,"●","●","●","●","●","●","●","●",null,"●","●","●","●","●","●","●","●","●","●","●"]
[65,null,null,null,"●","●","●","●","●","●",null,"●","●","●","●","●","●","●","●","●","●","●"]
[80,null,null,null,null,null,"●","●","●","●",null,"●","●",null,null,null,"●","●",null,null,"●","●","●","●"]
[100,null,null,null,null,null,null,null,"●","●",null,"●","●",null,null,null,"●","●",null,null,"●","●","●","●"]
[125,null,null,null,null,null,null,null,"●","●",null,"●","●",null,null,null,null,null,null,null,"●","●","●","●","●"]
[150,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]
[200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]
[250,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]
[300,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●"]
[400,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●"]

{"sheet":"KVs","index":36,"n_rows":20,"n_cols":43,"rows_kept":20,"cut":false,"hidden":false,"merged":[[1,2,1,6],[1,7,2,42],[2,2,2,6],[4,1,5,1],[4,3,4,6],[5,3,6,6],[7,3,8,6],[8,2,10,2],[9,3,11,6],[11,2,19,2],[12,3,12,6],[13,3,14,6],[15,3,17,6],[18,3,19,6]]}
[]
[null,null,"Ход штока клапана",null,null,null,null,"Условная пропускная способность, Kvу, м³/ч"]
[null,null,"Серия"]
[null,"ДУ, мм",110,100,200,210,220,0.16,0.25,0.4,0.63,1,1.6,2.5,3.2,4,5,6.3,8,10,12.5,16,20,25,32,40,50,63,80,100,125,160,200,250,360,400,450,630,800,1000,1250,1600,2000]
[null,15,5,null,null,null,null,"●","●","●","●","●","●","●","●","●"]
[null,null,null,10,null,null,null,null,null,null,null,null,"●","●",null,"●",null,"●",null,"●"]
[null,20,5,null,null,null,null,null,null,null,null,null,"●","●",null,"●","●","●","●","●"]
[null,25,7,20,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●",null,"●"]
[null,32,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●",null,"●"]
[null,40,null,25,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●",null,"●","●","●"]
[null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●","●","●","●","●"]
[null,65,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,null,null,null,null,"●","●","●"]
[null,80,null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●","●","●","●","●"]
[null,100,null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●",null,null,null,null,"●","●","●","●","●"]
[null,125,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●","●"]
[null,150,null,75,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●",null,"●","●"]
[null,200,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●",null,"●","●","●"]
[null,250,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]
[null,300,null,80,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]
[null,400,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"●","●","●"]

{"sheet":"Перепад","index":37,"n_rows":35,"n_cols":19,"rows_kept":35,"cut":false,"hidden":false,"merged":[[33,9,34,9],[33,10,34,10],[33,11,34,11],[29,3,30,3],[33,4,34,5],[33,6,34,6],[33,7,34,7],[33,8,34,8],[27,10,28,10],[27,11,28,11],[27,12,28,12],[33,12,34,12],[33,13,34,13],[27,13,28,13],[27,1,28,1],[27,2,28,2],[27,6,28,6],[27,7,28,7],[27,8,28,8],[23,1,24,1],[23,2,24,2],[23,4,24,4],[23,5,24,5],[23,6,24,6],[25,1,26,1],[25,6,26,6],[25,7,26,7],[25,8,26,8],[25,10,26,10],[20,11,21,11],[20,12,21,12],[23,8,24,8],[23,10,24,10],[25,2,26,2],[23,7,24,7],[25,11,26,11],[25,12,26,12],[11,10,12,10],[17,4,17,5],[17,8,17,9],[16,4,16,9],[18,7,19,7],[18,8,19,8],[11,4,12,4],[11,5,12,5],[11,6,12,6],[11,7,12,7],[11,8,12,8],[11,9,12,9],[4,4,4,7],[10,8,10,9],[5,4,6,4],[5,5,6,5],[5,6,6,6],[5,7,6,7],[16,12,17,12],[16,13,17,13],[22,1,22,18],[31,1,31,18],[32,3,34,3],[20,4,21,5],[20,6,21,6],[20,7,21,7],[18,12,19,12],[20,1,21,1],[20,2,21,2],[16,14,17,14],[20,13,21,13],[20,8,21,8],[20,9,21,9],[20,10,21,10],[16,1,19,1],[16,2,19,2],[3,1,3,18],[4,1,9,1],[4,2,9,2],[6,10,9,10],[6,11,9,11],[10,1,15,1],[10,2,15,2],[12,11,15,11],[5,8,6,8],[5,9,6,9],[16,15,17,15],[16,16,17,16],[16,17,17,17],[16,18,17,18]]}
[]
[null,"Допустимые перепады давления, ΔР, атм"]
[null,"Привод","Усилие, Н","Серия",15,20,25,32,40,50,65,80,100,125,150,200,250,300,400]
[]
[null,"ES05-11 (…/Е)",600,110,16,null,null,null,14,10]
[null,null,null,100,8.5,6.3,4,3.5,1.5]
[null,null,null,220]
[null,null,null,200]
[null,null,null,210]
[null,null,null,220]
[null,"ES05-12 (…/Е)",1000,110,null,null,null,null,16]
[null,null,null,100,14,10.5,6.5,6.2,4,2.5,5]
[null,null,null,220]
[null,null,null,200]
[null,null,null,210]
[null,null,null,220]
[null,"ES06-4 (…/Е)",2000,"110 СЧ",18]
[null,null,null,"110 ВЧ",25,null,20,16,16]
[null,null,null,"100, 200",null,null,13.5,10,9,7,10,8]
[null,null,null,"210, 220",null,null,13,null,null,16,12,10]
[null,"ES08 (…/Е)",4000,"100, 200",30,null,20,12,10,8,15,10,8,6]
[null,null,null,"210, 220"]
[]
[null,"ST mini",1100,"100, 200",15.5,11.6,7.4,6.8,5.8,2.5,8]
[null,null,null,"210, 220",null,null,null,null,null,8]
[null,"ST 0",4500,"100, 200",null,null,20,12,10,8,16,10,8]
[null,null,null,"210, 220",null,null,null,null,null,20]
[null,"ST 0,1",7500,"100, 200",null,null,30,25,18,15,21,16,14,10]
[null,null,null,"210, 220",null,null,null,null,null,25]
[null,"ST 1",8700,"100, 200, 210, 220",null,null,null,null,null,null,null,18,16,12,10,9,8]
[null,"ST 2",21500,null,null,null,null,null,null,null,null,null,null,18,16,14,12,6,4.5]
[]
[null,"AVM 322 S",1000,"100 200 210 220",14,8,7.4,6.2]
[null,"AVM 234 S",2000,null,16,null,13,10,9,15,12,8,6,5]
[null,"AVF 234 S ",2000,null,null,null,null,null,9,6.8,12,8,6,5]

{"sheet":"Диапазоны","index":38,"n_rows":32,"n_cols":28,"rows_kept":32,"cut":false,"hidden":false,"merged":[[0,23,0,27],[0,1,0,22],[1,1,1,2],[1,3,1,4],[1,5,1,6],[1,7,1,8],[1,9,1,10],[1,11,1,16],[1,17,1,22]]}
[null,"Danfoss",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"КПСР-Групп"]
[null,"AVP",null,"AVA",null,"AVD/AVDS",null,"AFP",null,"AFP-9",null,"AFA",null,null,null,null,null,"AFD"]
["атм","0,2 - 1","0,3 - 2","1 - 4,5","3 - 11","1 - 5","3 - 12","0,15-1,5","0,1 - 0,7","0,5 - 3","1 - 6","3 - 11","10 - 16","1 - 5","0,5 - 2,5","0,15-1,2","0,1 - 0,6","3 - 12","10 - 16","1 - 6","0,5 - 3","0,15-1,5","0,1-0,7",0,1,2,3,4]
[0.15]
[0.1]
[0.2]
[0.3]
[0.4]
[0.5]
[0.6]
[0.7]
[1]
[1.2]
[1.5]
[1.6]
[2]
[2.1]
[2.2000000000000002]
[2.5]
[3]
[4]
[4.0999999999999996]
[4.5]
[5]
[5.5]
[6]
[7]
[8]
[10]
[11]
[12]
[16]

{"sheet":"КПСР серия 100","index":39,"n_rows":46,"n_cols":24,"rows_kept":46,"cut":false,"hidden":true,"merged":[[39,0,41,0],[19,0,19,7],[20,2,21,2],[37,9,38,9],[35,2,36,2],[35,1,36,1],[30,1,32,1],[30,2,32,2],[27,9,29,9],[30,9,32,9],[27,0,38,0],[33,2,34,2],[33,1,34,1],[37,1,38,1],[37,2,38,2],[35,9,36,9],[16,0,18,0],[16,1,18,1],[16,2,18,2],[27,1,29,1],[27,2,29,2],[22,2,23,2],[24,2,25,2],[20,0,26,0],[6,3,6,4],[16,9,18,9],[22,9,23,9],[24,9,25,9],[33,9,34,9],[16,8,18,8],[16,3,17,4],[16,5,17,7],[16,10,17,23],[1,6,1,11],[2,6,2,11],[24,5,25,5],[24,7,25,7],[3,6,3,11],[20,9,21,9],[19,10,19,23]]}
[]
[null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР 1- Х - ХХ - Х.ХХХХ - СЧ - 1,6 - 1 - 150 - У"]
[]
["Серия 100",null,null,null,null,null,null,null,null,null,null,"Диаметр изделия",null,null,null,"Код привода"]
["Материал корпуса: Серый чугун (EN-JS 1040)"]
["Рабочее давление: 1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность"]
["Рабочая температура: max +150°С"]
[null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру уточняйте у сотрудников компании"]
[]
[]
["Производитель привода","Марка привода","Макс. усилие, Н","Управление",null,"Обратная связь ②",null,null,"Код привода","ход штока привода","Dn, мм"]
[]
[null,null,null,"трехточечное","аналоговое","1-100 Ω","0-10 v","4-20 mA",null,null,15,20,25,32,40,50,65,80,100,125,150,200,250,300]
[null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
["AUMA","ES 05-11",600,"+",null,null,null,null,"1.3500",30]
[null,"ES 05-11/E",null,null,"+",null,"+",null,"1.3502"]
[null,"ES 05-12",1000,"+",null,null,null,null,"1.3501",30]
[null,"ES 05-12/E",null,null,"+",null,"+",null,"1.3503",null,0.16]
[null,"ES 06-4",2000,"+",null,"②",null,"②","1.3600",35]
[null,"ES 06-4/E",null,null,"+",null,"+",null,"1.3601",null,0.25,null,1.6]
[null,"ES 08",4500,"+",null,null,null,null,"1.3700",null,null,null,null,null,null,10,null,null,63]
["REGADA","ST mini",1100,"+",null,null,null,null,"1.1100",25,0.4,1.6,2.5,null,10,null,25,40,null,100,null,250,400]
[null,null,null,"+",null,"+",null,null,"1.1114",null,null,null,null,6.3,null,16,null,null,80,null,160,null,null,1000]
[null,null,null,"+",null,null,null,"+","1.1109",null,0.63,2.5,4,null,16,null,32,63,null,125,null,360,630]
[null,"ST 0",4500,"+",null,null,null,null,"1.1200",40,null,null,null,10,null,25,null,null,100,null,280,null,null,1250]
[null,null,null,"+",null,"+",null,null,"1.1213",null,1,4,6.3,null,20,null,40,80,null,160,null,450,800]
[null,null,null,"+",null,null,null,"+","1.1212",null,null,null,null,16,null,32,null,null,125,null,360,null,null,1600]
[null,"ST 0.1",7500,"+",null,"+",null,null,"1.1300",50,1.6,6.3,8,null,25,null,63,100,null,250,null,630,1000]
[null,null,null,"+",null,null,null,"+","1.1309",null,null,null,null,null,null,40,null,null,160]
[null,"ST 1",8700,"+",null,"+",null,null,"1.1400",80,2.5,null,10]
[null,null,null,"+",null,null,"+",null,"1.1409"]
[null,"ST 2",21500,"+",null,"+",null,null,"1.1500",80,3.2]
[null,null,null,"+",null,null,"+",null,"1.1509"]
["SAUTER","AVM 322 ",1000,"+","+",null,null,"+","1.2300","20",4]
[null,"AVM 234",2000,"+","+",null,null,"+","1.2100","50"]
[null,"AVF 234 ③",2000,"+","+",null,null,"+","1.2200","50"]
[]
["① - стоимость на изделия Dn>100 предоставляется по запросу и после обработки опросного листа"]
["② - привода ES 06-4 и ES 06-4/E могут комплектоваться датчиками обратной связи 1-100 Ω и 4-20 mA по запросу"]
["③ - привод SAUTER AVF 234 имеет встроенную функцию безопасности при отключении питания (НЗ или НО) "]

{"sheet":"КПСР серия 110","index":40,"n_rows":31,"n_cols":21,"rows_kept":31,"cut":false,"hidden":true,"merged":[[27,6,28,6],[27,8,28,8],[27,9,28,9],[20,3,21,3],[20,4,21,4],[20,5,21,5],[20,6,21,6],[20,7,21,7],[20,8,21,8],[20,9,22,9],[27,7,28,7],[19,10,19,15],[20,0,28,0],[20,2,22,2],[27,1,28,1],[20,1,21,1],[25,5,26,5],[25,7,26,7],[25,9,26,9],[19,0,19,7],[23,2,24,2],[23,9,24,9],[25,2,26,2],[27,2,28,2],[27,3,28,3],[27,4,28,4],[27,5,28,5],[1,6,1,11],[2,6,2,11],[3,6,3,11],[6,3,6,4],[16,0,18,0],[16,1,18,1],[16,2,18,2],[16,3,17,4],[16,5,17,7],[16,8,18,8],[16,10,17,15],[16,9,18,9]]}
[]
[null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР 1- Х - ХХ - Х.ХХХХ - СЧ - 1,6 - 1 - 150 - У"]
[]
["Серия 110",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Диаметр изделия",null,null,null,"Код привода"]
["Материал корпуса: Серый чугун (EN-JS 1040), Высокопрочный чугун (EN-JS 1025)"]
["Рабочее давление: 1,6 МПа (16 атм), 2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность"]
["Рабочая температура: +150°С, +220°С"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру уточняйте у сотрудников компании"]
[]
[]
["Производитель привода","Марка привода","Макс. усилие, Н","Управление",null,"Обратная связь ②",null,null,"Код привода","ход штока привода","Dn, мм"]
[]
[null,null,null,"трехточечное","аналоговое","1-100 Ω","0-10 v","4-20 mA",null,null,15,20,25,32,40,50]
[null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
["AUMA","ES 05-11",600,"+",null,null,null,null,"1.3500",30,0.16]
[null,null,null,null,null,null,null,null,null,null,0.25,null,1.6]
[null,"ES 05-11/E",null,null,"+",null,"+",null,"1.3502",null,0.4,1.6,2.5,null,10,10]
[null,"ES 05-12",1000,"+",null,null,null,null,"1.3501",30,0.63,2.5,4,6.3,16,16]
[null,"ES 05-12/E",null,null,"+",null,"+",null,"1.3503",null,1,4,6.3,10,20,25]
[null,"ES 06-4",2000,"+",null,"②",null,"②","1.3600",35,1.6,6.3,8,16,25,32]
[null,"ES 06-4/E",null,null,"+",null,"+",null,"1.3601",null,2.5,null,10,null,null,40]
[null,"ES 08",4500,"+",null,null,null,null,"1.3700",null,3.2]
[null,null,null,null,null,null,null,null,null,null,4]
[]
["② - привода ES 06-4 и ES 06-4/E могут комплектоваться датчиками обратной связи 1-100 Ω и 4-20 mA по запросу"]

{"sheet":"КПСР серия 200","index":41,"n_rows":46,"n_cols":22,"rows_kept":46,"cut":false,"hidden":true,"merged":[[39,0,41,0],[16,10,17,21],[30,9,32,9],[33,1,34,1],[33,2,34,2],[33,9,34,9],[35,1,36,1],[35,2,36,2],[35,9,36,9],[24,2,25,2],[24,5,25,5],[24,7,25,7],[24,9,25,9],[27,0,38,0],[27,1,29,1],[27,2,29,2],[27,9,29,9],[30,1,32,1],[30,2,32,2],[37,1,38,1],[37,2,38,2],[37,9,38,9],[19,0,19,7],[19,10,19,21],[20,0,26,0],[20,2,21,2],[20,9,21,9],[22,2,23,2],[22,9,23,9],[1,6,1,11],[2,6,2,11],[3,6,3,11],[6,3,6,4],[16,0,18,0],[16,1,18,1],[16,2,18,2],[16,3,17,4],[16,5,17,7],[16,8,18,8],[16,9,18,9]]}
[]
[null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР 1- Х - ХХ - Х.ХХХХ - ВЧ - 2,5 - 1 - 220 - У"]
[]
["Серия 200",null,null,null,null,null,null,null,null,null,null,"Диаметр изделия",null,null,null,"Код привода"]
["Материал корпуса: Высокопрочный чугун (EN-JS 1025)"]
["Рабочее давление: 2,5 МПа (25 атм)",null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность"]
["Рабочая температура: max +220°С"]
[]
[]
[]
["Производитель привода","Марка привода","Макс. усилие, Н","Управление",null,"Обратная связь ②",null,null,"Код привода","ход штока привода","Dn, мм"]
[]
[null,null,null,"трехточечное","аналоговое","1-100 Ω","0-10 v","4-20 mA",null,null,15,20,25,32,40,50,65,80,100,125,150,200]
[null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
["AUMA","ES 05-11",600,"+",null,null,null,null,"1.3500",30]
[null,"ES 05-11/E",null,null,"+",null,"+",null,"1.3502"]
[null,"ES 05-12",1000,"+",null,null,null,null,"1.3501",30]
[null,"ES 05-12/E",null,null,"+",null,"+",null,"1.3503",null,0.16]
[null,"ES 06-4",2000,"+",null,"②",null,"②","1.3600",35]
[null,"ES 06-4/E",null,null,"+",null,"+",null,"1.3601",null,0.25,null,1.6]
[null,"ES 08",4500,"+",null,null,null,null,"1.3700",null,null,null,null,null,null,10,null,null,63]
["REGADA","ST mini",1100,"+",null,null,null,null,"1.1100",25,0.4,1.6,2.5,null,10,null,25,40,null,100,null,250]
[null,null,null,"+",null,"+",null,null,"1.1114",null,null,null,null,6.3,null,16,null,null,80,null,160]
[null,null,null,"+",null,null,null,"+","1.1109",null,0.63,2.5,4,null,16,null,32,63,null,125,null,360]
[null,"ST 0",4500,"+",null,null,null,null,"1.1200",40,null,null,null,10,null,25,null,null,100,null,280]
[null,null,null,"+",null,"+",null,null,"1.1213",null,1,4,6.3,null,20,null,40,80,null,160,null,450]
[null,null,null,"+",null,null,null,"+","1.1212",null,null,null,null,16,null,32,null,null,125,null,360]
[null,"ST 0.1",7500,"+",null,"+",null,null,"1.1300",50,1.6,6.3,8,null,25,null,63,100,null,250,null,630]
[null,null,null,"+",null,null,null,"+","1.1309",null,null,null,null,null,null,40,null,null,160]
[null,"ST 1",8700,"+",null,"+",null,null,"1.1400",80,2.5,null,10]
[null,null,null,"+",null,null,"+",null,"1.1409"]
[null,"ST 2",21500,"+",null,"+",null,null,"1.1500",80,3.2]
[null,null,null,"+",null,null,"+",null,"1.1509"]
["SAUTER","AVM 322 ",1000,"+","+",null,null,"+","1.2300",20,4]
[null,"AVM 234",2000,"+","+",null,null,"+","1.2100",50]
[null,"AVF 234 ③",2000,"+","+",null,null,"+","1.2200",50]
[]
["① - стоимость на изделия Dn>100 предоставляется по запросу и после обработки опросного листа"]
["② - привода ES 06-4 и ES 06-4/E могут комплектоваться датчиками обратной связи 1-100 Ω и 4-20 mA по запросу"]
["③ - привод SAUTER AVF 234 имеет встроенную функцию безопасности при отключении питания (НЗ или НО) "]

{"sheet":"КПСР серия 210","index":42,"n_rows":46,"n_cols":25,"rows_kept":46,"cut":false,"hidden":true,"merged":[[37,1,38,1],[37,2,38,2],[37,9,38,9],[39,0,41,0],[16,10,17,24],[19,10,19,24],[33,1,34,1],[33,2,34,2],[33,9,34,9],[35,1,36,1],[35,2,36,2],[35,9,36,9],[24,5,25,5],[24,7,25,7],[24,9,25,9],[27,0,38,0],[27,1,29,1],[27,2,29,2],[27,9,29,9],[30,1,32,1],[30,2,32,2],[30,9,32,9],[19,0,19,7],[20,0,26,0],[20,2,21,2],[20,9,21,9],[22,2,23,2],[22,9,23,9],[24,2,25,2],[1,6,1,11],[2,6,2,11],[3,6,3,11],[6,3,6,4],[16,0,18,0],[16,1,18,1],[16,2,18,2],[16,3,17,4],[16,5,17,7],[16,8,18,8],[16,9,18,9]]}
[]
[null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Клапан КПСР 1- Х - ХХ - Х.ХХХХ - CN - 4,0 - 1 - 260 - У"]
[]
["Серия 200",null,null,null,null,null,null,null,null,null,null,"Диаметр изделия",null,null,null,"Код привода"]
["Материал корпуса: Сталь 20 (GS-C25)"]
["Рабочее давление: 4,0 МПа (40 атм)",null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность"]
["Рабочая температура: max +260°С"]
[]
[]
[]
["Производитель привода","Марка привода","Макс. усилие, Н","Управление",null,"Обратная связь ②",null,null,"Код привода","ход штока привода","Dn, мм"]
[]
[null,null,null,"трехточечное","аналоговое","1-100 Ω","0-10 v","4-20 mA",null,null,15,20,25,32,40,50,65,80,100,125,150,200,250,300,400]
[null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
["AUMA","ES 05-11",600,"+",null,null,null,null,"1.3500",30]
[null,"ES 05-11/E",null,null,"+",null,"+",null,"1.3502"]
[null,"ES 05-12",1000,"+",null,null,null,null,"1.3501",30]
[null,"ES 05-12/E",null,null,"+",null,"+",null,"1.3503",null,0.16]
[null,"ES 06-4",2000,"+",null,"②",null,"②","1.3600",35]
[null,"ES 06-4/E",null,null,"+",null,"+",null,"1.3601",null,0.25,null,1.6]
[null,"ES 08",4500,"+",null,null,null,null,"1.3700",null,null,null,null,null,null,10,null,null,63]
["REGADA","ST mini",1100,"+",null,null,null,null,"1.1100",25,0.4,1.6,2.5,null,10,null,25,40,null,100,null,250,400,null,1250]
[null,null,null,"+",null,"+",null,null,"1.1114",null,null,null,null,6.3,null,16,null,null,80,null,160,null,null,1000]
[null,null,null,"+",null,null,null,"+","1.1109",null,0.63,2.5,4,null,16,null,32,63,null,125,null,360,630,null,1600]
[null,"ST 0",4500,"+",null,null,null,null,"1.1200",40,null,null,null,10,null,25,null,null,100,null,280,null,null,1200]
[null,null,null,"+",null,"+",null,null,"1.1213",null,1,4,6.3,null,20,null,40,80,null,160,null,450,800,null,2000]
[null,null,null,"+",null,null,null,"+","1.1212",null,null,null,null,16,null,32,null,null,125,null,360,null,null,1600]
[null,"ST 0.1",7500,"+",null,"+",null,null,"1.1300",50,1.6,6.3,8,null,25,null,63,100,null,250,null,630,1000,null,2500]
[null,null,null,"+",null,null,null,"+","1.1309",null,null,null,null,null,null,40,null,null,160]
[null,"ST 1",8700,"+",null,"+",null,null,"1.1400",80,2.5,null,10]
[null,null,null,"+",null,null,"+",null,"1.1409"]
[null,"ST 2",21500,"+",null,"+",null,null,"1.1500",80,3.2]
[null,null,null,"+",null,null,"+",null,"1.1509"]
["SAUTER","AVM 322 ",1000,"+","+",null,null,"+","1.2300",20,4]
[null,"AVM 234",2000,"+","+",null,null,"+","1.2100",50]
[null,"AVF 234 ③",2000,"+","+",null,null,"+","1.2200",50]
[]
["① - стоимость на изделия Dn>100 предоставляется по запросу и после обработки опросного листа"]
["② - привода ES 06-4 и ES 06-4/E могут комплектоваться датчиками обратной связи 1-100 Ω и 4-20 mA по запросу"]
["③ - привод SAUTER AVF 234 имеет встроенную функцию безопасности при отключении питания (НЗ или НО) "]

{"sheet":"КССР серия 100","index":43,"n_rows":46,"n_cols":19,"rows_kept":46,"cut":false,"hidden":true,"merged":[[1,6,1,11],[2,6,2,11],[3,6,3,11],[6,3,6,4],[16,0,18,0],[16,1,18,1],[16,2,18,2],[16,3,17,4],[16,5,17,7],[16,8,18,8],[16,9,18,9],[19,0,19,7],[20,0,26,0],[20,2,21,2],[20,9,21,9],[22,2,23,2],[22,9,23,9],[24,2,25,2],[27,1,29,1],[27,2,29,2],[27,9,29,9],[30,1,32,1],[30,2,32,2],[30,9,32,9],[37,1,38,1],[37,2,38,2],[37,9,38,9],[39,0,41,0],[16,10,17,18],[19,10,19,18],[33,1,34,1],[33,2,34,2],[33,9,34,9],[35,1,36,1],[35,2,36,2],[35,9,36,9],[24,5,25,5],[24,7,25,7],[24,9,25,9],[27,0,38,0]]}
[]
[null,null,null,null,null,null,"Номенклатура"]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
[null,null,null,null,null,null,null,null,null,null,null,"Клапан КССР 1- Х - ХХ - Х.ХХХХ - СЧ - 1,6 - 1 - 150 - У"]
[]
["Серия 100",null,null,null,null,null,null,null,null,null,null,"Диаметр изделия",null,null,null,"Код привода"]
["Материал корпуса: Серый чугун (EN-JS 1040)"]
["Рабочее давление: 1,6 МПа (16 атм)",null,null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность"]
["Рабочая температура: max +150°С"]
[null,null,null,null,null,null,null,null,null,null,"Применяемость приводов к конкретному диаметру уточняйте у сотрудников компании"]
[]
[]
["Производитель привода","Марка привода","Макс. усилие, Н","Управление",null,"Обратная связь ②",null,null,"Код привода","ход штока привода","Dn, мм"]
[]
[null,null,null,"трехточечное","аналоговое","1-100 Ω","0-10 v","4-20 mA",null,null,15,20,25,32,40,50,65,80,100]
[null,null,null,null,null,null,null,null,null,null,"Условная пропускная способность, м³/ч"]
["AUMA","ES 05-11",600,"+",null,null,null,null,"1.3500",30]
[null,"ES 05-11/E",null,null,"+",null,"+",null,"1.3502"]
[null,"ES 05-12",1000,"+",null,null,null,null,"1.3501",30]
[null,"ES 05-12/E",null,null,"+",null,"+",null,"1.3503",null,0.16]
[null,"ES 06-4",2000,"+",null,"②",null,"②","1.3600",35]
[null,"ES 06-4/E",null,null,"+",null,"+",null,"1.3601",null,0.25,null,1.6]
[null,"ES 08",4500,"+",null,null,null,null,"1.3700",null,null,null,null,null,null,10,null,null,63]
["REGADA","ST mini",1100,"+",null,null,null,null,"1.1100",25,0.4,1.6,2.5,null,10,null,25,40]
[null,null,null,"+",null,"+",null,null,"1.1114",null,null,null,null,6.3,null,16,null,null,80]
[null,null,null,"+",null,null,null,"+","1.1109",null,0.63,2.5,4,null,16,null,32,63]
[null,"ST 0",4500,"+",null,null,null,null,"1.1200",40,null,null,null,10,null,25,null,null,100]
[null,null,null,"+",null,"+",null,null,"1.1213",null,1,4,6.3,null,20,null,40,80]
[null,null,null,"+",null,null,null,"+","1.1212",null,null,null,null,16,null,32,null,null,125]
[null,"ST 0.1",7500,"+",null,"+",null,null,"1.1300",50,1.6,6.3,8,null,25,null,63,100]
[null,null,null,"+",null,null,null,"+","1.1309",null,null,null,null,null,null,40,null,null,160]
[null,"ST 1",8700,"+",null,"+",null,null,"1.1400",80,2.5,null,10]
[null,null,null,"+",null,null,"+",null,"1.1409"]
[null,"ST 2",21500,"+",null,"+",null,null,"1.1500",80,3.2]
[null,null,null,"+",null,null,"+",null,"1.1509"]
["SAUTER","AVM 322 ",1000,"+","+",null,null,"+","1.2300","20",4]
[null,"AVM 234",2000,"+","+",null,null,"+","1.2100","50"]
[null,"AVF 234 ③",2000,"+","+",null,null,"+","1.2200","50"]
[]
["① - стоимость на изделия Dn>100 предоставляется по запросу и после обработки опросного листа"]
["② - привода ES 06-4 и ES 06-4/E могут комплектоваться датчиками обратной связи 1-100 Ω и 4-20 mA по запросу"]
["③ - привод SAUTER AVF 234 имеет встроенную функцию безопасности при отключении питания (НЗ или НО) "]

{"sheet":"РА серия 100,200","index":44,"n_rows":36,"n_cols":22,"rows_kept":36,"cut":false,"hidden":true,"merged":[[0,6,0,10],[1,6,1,10],[2,6,2,10],[5,3,5,4],[16,0,18,0],[16,1,18,1],[16,2,18,2],[16,3,18,3],[16,4,18,4],[16,19,18,19],[16,20,18,20],[16,21,18,21],[19,0,35,0],[19,2,35,2],[16,5,17,16],[16,17,18,17],[16,18,18,18],[19,20,35,20],[19,21,35,21],[19,3,35,3],[19,4,35,4],[19,1,35,1],[19,17,35,17],[19,18,35,18],[19,19,35,19]]}
[null,null,null,null,null,null,"ПРАЙС-ЛИСТ "]
[null,null,null,null,null,null,"на продукцию \"КПСР Групп\""]
[null,null,null,null,null,null,"с \"01\" сентября 2016 г."]
[]
[null,null,null,null,null,null,null,null,null,"Маркировка изделия"]
[]
["Регулятор давления",null,null,null,null,null,null,"Регулятор РА - X   DN - KV - Y - XX - T -У"]
["РА",null,null,null,null,null,null,null,null,null,null,null,"Рабочая температура"]
["В комплект поставки входит необходимый \"Монтажный комплект\"",null,null,null,null,null,null,"Тип регулятора"]
["Диапазоны настройки:",null,null,null,null,null,null,null,null,null,null,null,"Материал корпуса "]
[0,"- от 0,01 до 0,1 Мпа (цвет пружины - СЕРЫЙ)",null,null,null,null,null,"Диаметр регулятора"]
[1,"- от 0,04 до 0,16 Мпа (цвет пружины - ЖЕЛТЫЙ)",null,null,null,null,null,null,null,null,null,"Диапазон настройки"]
[2,"- от 0,1 до 0,4 Мпа (цвет пружины - КРАСНЫЙ)",null,null,null,null,null,"Условная пропускная способность"]
[3,"- от 0,3 до 0,7 Мпа (цвет пружины - СИНИЙ)"]
[4,"- от 0,6 до 1,2 Мпа (цвет пружины - ЧЕРНЫЙ)"]
[]
["Серия","Тип регулятора","Метериал корпуса","Рабочее давление, Мпа","Рабочая температура","Dn, мм",null,null,null,null,null,null,null,null,null,null,null,"Рабочая температура","Рабочее давление, Мпа","Метериал корпуса","Тип регулятора","Серия"]
[]
[null,null,null,null,null,15,20,25,32,40,50,65,80,100,125,150,200]
["Серия 100","РА-М          РА-А           РА-В","СЧ",1.6,"+150°С",0.16,null,null,null,null,null,null,null,null,null,null,null,"+220°С",2.5,"ВЧ","РА-А","Серия 200"]
[]
[null,null,null,null,null,0.25,null,1.6]
[null,null,null,null,null,null,null,null,null,null,10,null,null,63]
[null,null,null,null,null,0.4,1.6,2.5,null,10,null,25,40,null,100,null,250]
[null,null,null,null,null,null,null,null,6.3,null,16,null,null,80,null,160]
[null,null,null,null,null,0.63,2.5,4,null,16,null,32,63,null,125,null,360]
[null,null,null,null,null,null,null,null,10,null,25,null,null,100,null,280]
[null,null,null,null,null,1,4,6.3,null,20,null,40,80,null,160,null,450]
[null,null,null,null,null,null,null,null,16,null,32,null,null,125,null,360]
[null,null,null,null,null,1.6,6.3,8,null,25,null,63,100,null,250,null,630]
[null,null,null,null,null,null,null,null,null,null,40,null,null,160]
[null,null,null,null,null,2.5,null,10]
[]
[null,null,null,null,null,3.2]
[]
[null,null,null,null,null,4]